## Complete Map
Fronius Gen24 Primo/Symo Inverter Register Map with Integer+SF Inverter Model and storage configured for ROW use
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Primo GEN24 6.0 Primo GEN24 10.0 Primo GEN24 10.0 208-240 Primo GEN24 3.0 Primo GEN24 3.6 Primo GEN24 3.8 208-240 Primo GEN24 4.0 Primo GEN24 4.6 Primo GEN24 5.0 Primo GEN24 6.0 208-240 Symo GEN24 10.0 Symo GEN24 3.0 Symo GEN24 4.0 Symo GEN24 5.0 Symo GEN24 6.0 Symo GEN24 8.0
40037 | 40044 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (10x) | uint16 |  |  | 101, 103
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model inverter (10x) | uint16 | Registers |  | 50
40072 | 40072 | 1 | R | 0x03 | A | AC Current | uint16 | A | A_SF
40073 | 40073 | 1 | R | 0x03 | AphA | Phase A Current | uint16 | A | A_SF
40074 | 40074 | 1 | R | 0x03 | AphB | Phase B Current | uint16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection.
40075 | 40075 | 1 | R | 0x03 | AphC | Phase C Current | uint16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection.
40076 | 40076 | 1 | R | 0x03 | A_SF |  | sunssf |  |  | auto-scaled on A, AphA, AphB, AphC
40077 | 40077 | 1 | R | 0x03 | PPVphAB | Phase Voltage AB | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
40078 | 40078 | 1 | R | 0x03 | PPVphBC | Phase Voltage BC | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
40079 | 40079 | 1 | R | 0x03 | PPVphCA | Phase Voltage CA | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
40080 | 40080 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | uint16 | V | V_SF
40081 | 40081 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
40082 | 40082 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
40083 | 40083 | 1 | R | 0x03 | V_SF |  | sunssf |  |  | -1
40084 | 40084 | 1 | R | 0x03 | W | AC Power | int16 | W | W_SF
40085 | 40085 | 1 | R | 0x03 | W_SF |  | sunssf |  |  | auto-scaled on W
40086 | 40086 | 1 | R | 0x03 | Hz | Line Frequency | uint16 | Hz | Hz_SF
40087 | 40087 | 1 | R | 0x03 | Hz_SF |  | sunssf |  |  | -2
40088 | 40088 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
40089 | 40089 | 1 | R | 0x03 | VA_SF |  | sunssf |  |  | auto-scaled on VA
40090 | 40090 | 1 | R | 0x03 | VAr | AC Reactive Power | int16 | var | VAr_SF
40091 | 40091 | 1 | R | 0x03 | VAr_SF |  | sunssf |  |  | auto-scaled on VAr
40092 | 40092 | 1 | R | 0x03 | PF | AC Power Factor | int16 | Pct | PF_SF
40093 | 40093 | 1 | R | 0x03 | PF_SF |  | sunssf |  |  | -1
40094 | 40095 | 2 | R | 0x03 | WH | AC Energy | acc32 | Wh | WH_SF
40096 | 40096 | 1 | R | 0x03 | WH_SF |  | sunssf |  |  | auto-scaled
40097 | 40097 | 1 | R | 0x03 | DCA | DC Current | uint16 | A | DCA_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40098 | 40098 | 1 | R | 0x03 | DCA_SF |  | sunssf |  |  | not supported
40099 | 40099 | 1 | R | 0x03 | DCV | DC Voltage | uint16 | V | DCV_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
40100 | 40100 | 1 | R | 0x03 | DCV_SF |  | sunssf |  |  | not supported
40101 | 40101 | 1 | R | 0x03 | DCW | DC Power | int16 | W | DCW_SF
40102 | 40102 | 1 | R | 0x03 | DCW_SF |  | sunssf |  |  | auto-scaled on DCW
40103 | 40103 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF
40104 | 40104 | 1 | R | 0x03 | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | not supported
40105 | 40105 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | not supported
40106 | 40106 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | C | Tmp_SF | not supported
40107 | 40107 | 1 | R | 0x03 | Tmp_SF |  | sunssf |  |  | -1
40108 | 40108 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40109 | 40109 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
40110 | 40111 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
40112 | 40113 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
40114 | 40115 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
40116 | 40117 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
40118 | 40119 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
40120 | 40121 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40122 | 40122 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
40123 | 40123 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
40124 | 40124 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 82 (PV_STOR)
40125 | 40125 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40126 | 40126 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
40127 | 40127 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40128 | 40128 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
40129 | 40129 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40130 | 40130 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF
40131 | 40131 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF
40132 | 40132 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40133 | 40133 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40134 | 40134 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40135 | 40135 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40136 | 40136 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40137 | 40137 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40138 | 40138 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | from -1.0 to 0
40139 | 40139 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
40140 | 40140 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40141 | 40141 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF
40142 | 40142 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf
40143 | 40143 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
40144 | 40144 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
40145 | 40145 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF
40146 | 40146 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | 0
40147 | 40147 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF
40148 | 40148 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | 0
40149 | 40149 | 1 | R | 0x03 | Pad | Pad register. | pad
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40150 | 40150 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
40151 | 40151 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
40152 | 40152 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
40153 | 40153 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
40154 | 40154 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
40155 | 40155 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
40156 | 40156 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
40157 | 40157 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
40158 | 40158 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
40159 | 40159 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
40160 | 40160 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
40161 | 40161 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
40162 | 40162 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
40163 | 40163 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
40164 | 40164 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
40165 | 40165 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
40166 | 40166 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
40167 | 40167 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
40168 | 40168 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
40169 | 40169 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
40170 | 40170 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
40171 | 40171 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
40172 | 40172 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
40173 | 40173 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40174 | 40174 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40175 | 40175 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
40176 | 40176 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
40177 | 40177 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40178 | 40178 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
40179 | 40179 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40180 | 40180 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
40181 | 40181 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40182 | 40182 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
40183 | 40183 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
40184 | 40184 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40185 | 40185 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
40186 | 40186 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
40187 | 40190 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40191 | 40194 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
40195 | 40198 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
40199 | 40202 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
40203 | 40206 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
40207 | 40210 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
40211 | 40211 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
40212 | 40212 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
40213 | 40213 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
40214 | 40214 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
40215 | 40216 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
40217 | 40218 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40219 | 40222 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
40223 | 40224 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40225 | 40225 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
40226 | 40226 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
40227 | 40227 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40228 | 40228 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
40229 | 40229 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
40230 | 40230 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
40231 | 40231 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
40232 | 40232 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
40233 | 40233 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
40234 | 40234 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
40235 | 40235 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
40236 | 40236 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40237 | 40237 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40238 | 40238 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
40239 | 40239 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40243 | 40243 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
40245 | 40245 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
40249 | 40249 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40251 | 40251 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40252 | 40252 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40253 | 40253 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40254 | 40254 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
40255 | 40255 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 88
40256 | 40256 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
40257 | 40257 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
40258 | 40258 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
40259 | 40259 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
40260 | 40261 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
40262 | 40262 | 1 | R | 0x03 | N | Number of Modules | count |  |  | 4
40263 | 40263 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
40264 | 40264 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
40265 | 40272 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
40273 | 40273 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
40274 | 40274 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
40275 | 40275 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
40276 | 40277 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40278 | 40279 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40280 | 40280 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
40281 | 40281 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
40282 | 40283 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
40284 | 40284 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
40285 | 40292 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40293 | 40293 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
40294 | 40294 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
40295 | 40295 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
40296 | 40297 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
40298 | 40299 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40300 | 40300 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
40301 | 40301 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
40302 | 40303 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
40304 | 40304 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
40305 | 40312 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'StCha 3'
40313 | 40313 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF | When the battery is discharged the data-points of the charge input are set to 0
40314 | 40314 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
40315 | 40315 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF | When the battery is discharged the data-points of the charge input are set to 0
40316 | 40317 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Charge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
40318 | 40319 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40320 | 40320 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
40321 | 40321 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
40322 | 40323 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
40324 | 40324 | 1 | R | 0x03 | module/4/ID | Input ID | uint16 |  |  | 4
40325 | 40332 | 8 | R | 0x03 | module/4/IDStr | Input ID Sting | string |  |  | 'StDisCha 4'
40333 | 40333 | 1 | R | 0x03 | module/4/DCA | DC Current | uint16 | A | DCA_SF | When the battery is charged the data-points of the discharge input are set to 0
40334 | 40334 | 1 | R | 0x03 | module/4/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
40335 | 40335 | 1 | R | 0x03 | module/4/DCW | DC Power | uint16 | W | DCW_SF | When the battery is charged the data-points of the discharge input are set to 0
40336 | 40337 | 2 | R | 0x03 | module/4/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Discharge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
40338 | 40339 | 2 | R | 0x03 | module/4/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
40340 | 40340 | 1 | R | 0x03 | module/4/Tmp | Temperature | int16 | C |  | not supported
40341 | 40341 | 1 | R | 0x03 | module/4/DCSt | Operating State | enum16 |  |  | not supported
40342 | 40343 | 2 | R | 0x03 | module/4/DCEvt | Module Events | bitfield32 |  |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40344 | 40344 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model storage (124) | uint16 |  |  | 124
40345 | 40345 | 1 | R | 0x03 | L | Length of sunspec model storage (124) | uint16 | Registers |  | 24
40346 | 40346 | 1 | R | 0x03 | WChaMax | Setpoint for maximum charge. Additional Fronius description: Reference Value for maximum Charge and Discharge. Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. Every rate between this two limits is allowed. The inverter is not fully capable of transferring power as reported by this reference value. Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only | uint16 | W | WChaMax_SF
40347 | 40347 | 1 | R | 0x03 | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
40348 | 40348 | 1 | R | 0x03 | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
40349 | 40349 | 1 | RW | 0x03 0x06 0x10 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. Additional Fronius description: Active hold/discharge/charge storage control mode. Set the charge field to enable charging and the discharge field to enable discharging. | bitfield16 |  |  | bit 0: CHARGE bit 1: DiSCHARGE
40350 | 40350 | 1 | RW | 0x03 0x06 0x10 | VAChaMax | Setpoint for maximum charging VA. | uint16 | VA | VAChaMax_SF
40351 | 40351 | 1 | RW | 0x03 0x06 0x10 | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 | % WChaMax | MinRsvPct_SF
40352 | 40352 | 1 | R | 0x03 | ChaState | Currently available energy as a percent of the capacity rating. | uint16 | % AhrRtg | ChaState_SF
40353 | 40353 | 1 | R | 0x03 | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | uint16 | AH | StorAval_SF | not supported
40354 | 40354 | 1 | R | 0x03 | InBatV | Internal battery voltage. | uint16 | V | InBatV_SF | not supported
40355 | 40355 | 1 | R | 0x03 | ChaSt | Charge status of storage device. Enumerated value. | enum16 |  |  | 1: OFF 2: EMPTY 3: DISCHAGING 4: CHARGING 5: FULL 6: HOLDING 7: TESTING The status TESTING is used during battery calibration or service charge.
40356 | 40356 | 1 | RW | 0x03 0x06 0x10 | OutWRte | Percent of max discharge rate. Additional Fronius description: Defines maximum Discharge rate. If not used than the default is 100 and WChaMax defines max. Discharge rate. See WChaMax for details | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
40357 | 40357 | 1 | RW | 0x03 0x06 0x10 | InWRte | Percent of max charging rate. Additional Fronius description: Defines maximum Charge rate. If not used than the default is 100 and WChaMax defines max. Charge rate. See WChaMax for details | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
40358 | 40358 | 1 | R | 0x03 | InOutWRte_WinTms | Time window for charge/discharge rate change. | uint16 | Secs |  | not supported
40359 | 40359 | 1 | RW | 0x03 0x06 0x10 | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | uint16 | Secs |  | 0 - 28800
40360 | 40360 | 1 | R | 0x03 | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | not supported
40361 | 40361 | 1 | RW | 0x03 0x06 0x10 | ChaGriSet |  | enum16 |  |  | 0: PV (Charging from grid disabled) 1: GRID (Charging from grid enabled)
40362 | 40362 | 1 | R | 0x03 | WChaMax_SF | Scale factor for maximum charge. | sunssf |  |  | 0
40363 | 40363 | 1 | R | 0x03 | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | sunssf |  |  | 0
40364 | 40364 | 1 | R | 0x03 | VAChaMax_SF | Scale factor for maximum charging VA. | sunssf |  |  | not supported
40365 | 40365 | 1 | R | 0x03 | MinRsvPct_SF | Scale factor for minimum reserve percentage. | sunssf |  |  | -2
40366 | 40366 | 1 | R | 0x03 | ChaState_SF | Scale factor for available energy percent. | sunssf |  |  | -2
40367 | 40367 | 1 | R | 0x03 | StorAval_SF | Scale factor for state of charge. | sunssf |  |  | not supported
40368 | 40368 | 1 | R | 0x03 | InBatV_SF | Scale factor for battery voltage. | sunssf |  |  | not supported
40369 | 40369 | 1 | R | 0x03 | InOutWRte_SF | Scale factor for percent charge/discharge rate. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40370 | 40370 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40371 | 40371 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Manufacturer | string |  |  | Fronius
19 | 34 | 16 | R | 0x03 | Md | Device | string |  |  | e.g. Primo GEN24 6.0 Primo GEN24 10.0 Primo GEN24 10.0 208-240 Primo GEN24 3.0 Primo GEN24 3.6 Primo GEN24 3.8 208-240 Primo GEN24 4.0 Primo GEN24 4.6 Primo GEN24 5.0 Primo GEN24 6.0 208-240 Symo GEN24 10.0 Symo GEN24 3.0 Symo GEN24 4.0 Symo GEN24 5.0 Symo GEN24 6.0 Symo GEN24 8.0
35 | 42 | 8 | R | 0x03 | Opt | Options | string |  |  | not supported
43 | 50 | 8 | R | 0x03 | Vr | SW version of inverter | string |  |  | e.g. 1.8.10-0
51 | 66 | 16 | R | 0x03 | SN | Serialnumber of the inverter | string |  |  | e.g. 12345678
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## inverter (10x)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model inverter (10x) | uint16 |  |  | 101, 103
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model inverter (10x) | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | A | AC Current | uint16 | A | A_SF
4 | 4 | 1 | R | 0x03 | AphA | Phase A Current | uint16 | A | A_SF
5 | 5 | 1 | R | 0x03 | AphB | Phase B Current | uint16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection.
6 | 6 | 1 | R | 0x03 | AphC | Phase C Current | uint16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection.
7 | 7 | 1 | R | 0x03 | A_SF |  | sunssf |  |  | auto-scaled on A, AphA, AphB, AphC
8 | 8 | 1 | R | 0x03 | PPVphAB | Phase Voltage AB | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
9 | 9 | 1 | R | 0x03 | PPVphBC | Phase Voltage BC | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
10 | 10 | 1 | R | 0x03 | PPVphCA | Phase Voltage CA | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
11 | 11 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | uint16 | V | V_SF
12 | 12 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
13 | 13 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | uint16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection.
14 | 14 | 1 | R | 0x03 | V_SF |  | sunssf |  |  | -1
15 | 15 | 1 | R | 0x03 | W | AC Power | int16 | W | W_SF
16 | 16 | 1 | R | 0x03 | W_SF |  | sunssf |  |  | auto-scaled on W
17 | 17 | 1 | R | 0x03 | Hz | Line Frequency | uint16 | Hz | Hz_SF
18 | 18 | 1 | R | 0x03 | Hz_SF |  | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
20 | 20 | 1 | R | 0x03 | VA_SF |  | sunssf |  |  | auto-scaled on VA
21 | 21 | 1 | R | 0x03 | VAr | AC Reactive Power | int16 | var | VAr_SF
22 | 22 | 1 | R | 0x03 | VAr_SF |  | sunssf |  |  | auto-scaled on VAr
23 | 23 | 1 | R | 0x03 | PF | AC Power Factor | int16 | Pct | PF_SF
24 | 24 | 1 | R | 0x03 | PF_SF |  | sunssf |  |  | -1
25 | 26 | 2 | R | 0x03 | WH | AC Energy | acc32 | Wh | WH_SF
27 | 27 | 1 | R | 0x03 | WH_SF |  | sunssf |  |  | auto-scaled
28 | 28 | 1 | R | 0x03 | DCA | DC Current | uint16 | A | DCA_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
29 | 29 | 1 | R | 0x03 | DCA_SF |  | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | DCV | DC Voltage | uint16 | V | DCV_SF | not supported if the inverter has multiple DC inputs current of DC-strings can be found in MPPT model 160
31 | 31 | 1 | R | 0x03 | DCV_SF |  | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | DCW | DC Power | int16 | W | DCW_SF
33 | 33 | 1 | R | 0x03 | DCW_SF |  | sunssf |  |  | auto-scaled on DCW
34 | 34 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | C | Tmp_SF
35 | 35 | 1 | R | 0x03 | TmpSnk | Heat Sink Temperature | int16 | C | Tmp_SF | not supported
36 | 36 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | C | Tmp_SF | not supported
37 | 37 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | C | Tmp_SF | not supported
38 | 38 | 1 | R | 0x03 | Tmp_SF |  | sunssf |  |  | -1
39 | 39 | 1 | R | 0x03 | St | Enumerated value. Operating state | enum16 |  |  | see all states in our Modbus TCP & RTU user manual under SunSpec Operating Codes
40 | 40 | 1 | R | 0x03 | StVnd | Vendor specific operating state code | enum16 |  |  | same as register "St"
41 | 42 | 2 | R | 0x03 | Evt1 | Bitmask value. Event fields | bitfield32
43 | 44 | 2 | R | 0x03 | Evt2 | Reserved for future use | bitfield32
45 | 46 | 2 | R | 0x03 | EvtVnd1 | Vendor defined events | bitfield32 |  |  | "Customer" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Customer". If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels.
47 | 48 | 2 | R | 0x03 | EvtVnd2 | Vendor defined events | bitfield32 |  |  | "Technician" event severity level bitfield bit 0 -> Error bit 1 -> Warning bit 2 -> Info This bitfield is composed as a superposition for the severity-levels of all currently active events on view level "Technician" If a bit is set it means that currently there is at least one active event with this severity level. Multiple bits can be set at once indicating several active events with different severity-levels. View level "Technician" is a superset of view level "Customer". This means that all events visible for view level "Customer" are also visible for view level "Technician".
49 | 50 | 2 | R | 0x03 | EvtVnd3 | Vendor defined events | bitfield32 |  |  | not supported
51 | 52 | 2 | R | 0x03 | EvtVnd4 | Vendor defined events | bitfield32 |  |  | not supported

## nameplate (120)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model nameplate (120) | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model nameplate (120) | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 82 (PV_STOR)
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 1
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 1
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF | from -1.0 to 0
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | from 0 to 1.0
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | from -1.0 to 0
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF | from 0 to 1.0
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf
22 | 22 | 1 | R | 0x03 | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | 0
28 | 28 | 1 | R | 0x03 | Pad | Pad register. | pad

## settings (121)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model settings (121) | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model settings (121) | uint16 | Registers |  | 30
3 | 3 | 1 | R | 0x03 | WMax | Setting for maximum power output. Default to WRtg. | uint16 | W | WMax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | R | 0x03 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF | 0.0
6 | 6 | 1 | R | 0x03 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | not supported
7 | 7 | 1 | R | 0x03 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to VARtg. | uint16 | VA | VAMax_SF | same as nameplate.VARtg
9 | 9 | 1 | R | 0x03 | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ1
10 | 10 | 1 | R | 0x03 | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ2
11 | 11 | 1 | R | 0x03 | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ3
12 | 12 | 1 | R | 0x03 | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | int16 | var | VArMax_SF | same as nameplate.VArRtgQ4
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/sec | WGra_SF | not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ1
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ2
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ3
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF | same as nameplate.PFRtgQ4
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for real power. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for apparent power. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VArMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | not supported

## status (122)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model status (122) | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model status (122) | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | Bit 0: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | var | WAval_SF | not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. | bitfield32 |  |  | not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | bits are set according to enabled controls in immediate controls model 123 Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | string |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating active ride-through status. | bitfield16 |  |  | not supported
45 | 45 | 1 | R | 0x03 | Ris | Isolation resistance. | uint16 | ohms | Ris_SF
46 | 46 | 1 | R | 0x03 | Ris_SF | Scale factor for isolation resistance. | sunssf |  |  | auto-scaled on Ris

## controls (123)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model controls (123) | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model controls (123) | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs |  | 0 - 300
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs |  | 0 - 28800
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | enum16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF | 0% - 100%
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | from -1.0 to nameplate.PFRtgQ1 and from nameplate.PFRtgQ4 to +1.0
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 - 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 - 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of WMax. | int16 | % WMax | VArPct_SF | not supported
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of VArMax. | int16 | % VArMax | VArPct_SF | -100% - +100%
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of VArAval. | int16 | % VArAval | VArPct_SF | not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 - 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 - 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR percent limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power percent. | sunssf |  |  | 0

## mppt (160)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model mppt (160) | uint16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model mppt (160) | uint16 | Registers |  | 88
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf |  |  | auto-scaled on DCA 1-N
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf |  |  | auto-scaled on DCV 1-N
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf |  |  | auto-scaled on DCW 1-N
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | auto-scaled on DCWH 1-N
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32 |  |  | not supported
9 | 9 | 1 | R | 0x03 | N | Number of Modules | count |  |  | 4
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | module/1/ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | module/1/IDStr | Input ID Sting | string |  |  | 'MPPT 1'
20 | 20 | 1 | R | 0x03 | module/1/DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | module/1/DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | module/1/DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | module/1/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
25 | 26 | 2 | R | 0x03 | module/1/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
27 | 27 | 1 | R | 0x03 | module/1/Tmp | Temperature | int16 | C |  | not supported
28 | 28 | 1 | R | 0x03 | module/1/DCSt | Operating State | enum16 |  |  | not supported
29 | 30 | 2 | R | 0x03 | module/1/DCEvt | Module Events | bitfield32 |  |  | not supported
31 | 31 | 1 | R | 0x03 | module/2/ID | Input ID | uint16 |  |  | 2
32 | 39 | 8 | R | 0x03 | module/2/IDStr | Input ID Sting | string |  |  | 'MPPT 2'
40 | 40 | 1 | R | 0x03 | module/2/DCA | DC Current | uint16 | A | DCA_SF
41 | 41 | 1 | R | 0x03 | module/2/DCV | DC Voltage | uint16 | V | DCV_SF
42 | 42 | 1 | R | 0x03 | module/2/DCW | DC Power | uint16 | W | DCW_SF
43 | 44 | 2 | R | 0x03 | module/2/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF
45 | 46 | 2 | R | 0x03 | module/2/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
47 | 47 | 1 | R | 0x03 | module/2/Tmp | Temperature | int16 | C |  | not supported
48 | 48 | 1 | R | 0x03 | module/2/DCSt | Operating State | enum16 |  |  | not supported
49 | 50 | 2 | R | 0x03 | module/2/DCEvt | Module Events | bitfield32 |  |  | not supported
51 | 51 | 1 | R | 0x03 | module/3/ID | Input ID | uint16 |  |  | 3
52 | 59 | 8 | R | 0x03 | module/3/IDStr | Input ID Sting | string |  |  | 'StCha 3'
60 | 60 | 1 | R | 0x03 | module/3/DCA | DC Current | uint16 | A | DCA_SF | When the battery is discharged the data-points of the charge input are set to 0
61 | 61 | 1 | R | 0x03 | module/3/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
62 | 62 | 1 | R | 0x03 | module/3/DCW | DC Power | uint16 | W | DCW_SF | When the battery is discharged the data-points of the charge input are set to 0
63 | 64 | 2 | R | 0x03 | module/3/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is discharged the data-points of the charge input are set to 0 since software version 1.31: Charge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
65 | 66 | 2 | R | 0x03 | module/3/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
67 | 67 | 1 | R | 0x03 | module/3/Tmp | Temperature | int16 | C |  | not supported
68 | 68 | 1 | R | 0x03 | module/3/DCSt | Operating State | enum16 |  |  | not supported
69 | 70 | 2 | R | 0x03 | module/3/DCEvt | Module Events | bitfield32 |  |  | not supported
71 | 71 | 1 | R | 0x03 | module/4/ID | Input ID | uint16 |  |  | 4
72 | 79 | 8 | R | 0x03 | module/4/IDStr | Input ID Sting | string |  |  | 'StDisCha 4'
80 | 80 | 1 | R | 0x03 | module/4/DCA | DC Current | uint16 | A | DCA_SF | When the battery is charged the data-points of the discharge input are set to 0
81 | 81 | 1 | R | 0x03 | module/4/DCV | DC Voltage | uint16 | V | DCV_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Voltage of the inverter's battery port (regardless if the battery is currently charging or discharging)
82 | 82 | 1 | R | 0x03 | module/4/DCW | DC Power | uint16 | W | DCW_SF | When the battery is charged the data-points of the discharge input are set to 0
83 | 84 | 2 | R | 0x03 | module/4/DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | up to software version 1.30: When the battery is charged the data-points of the discharge input are set to 0 since software version 1.31: Discharge energy counter of the inverter's battery port (regardless if the battery is currently charging or discharging)
85 | 86 | 2 | R | 0x03 | module/4/Tms | Timestamp | uint32 | Secs |  | number of seconds since Jan 1st 2000 00:00 am
87 | 87 | 1 | R | 0x03 | module/4/Tmp | Temperature | int16 | C |  | not supported
88 | 88 | 1 | R | 0x03 | module/4/DCSt | Operating State | enum16 |  |  | not supported
89 | 90 | 2 | R | 0x03 | module/4/DCEvt | Module Events | bitfield32 |  |  | not supported

## storage (124)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model storage (124) | uint16 |  |  | 124
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model storage (124) | uint16 | Registers |  | 24
3 | 3 | 1 | R | 0x03 | WChaMax | Setpoint for maximum charge. Additional Fronius description: Reference Value for maximum Charge and Discharge. Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. Every rate between this two limits is allowed. The inverter is not fully capable of transferring power as reported by this reference value. Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only | uint16 | W | WChaMax_SF
4 | 4 | 1 | R | 0x03 | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
5 | 5 | 1 | R | 0x03 | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100%
6 | 6 | 1 | RW | 0x03 0x06 0x10 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. Additional Fronius description: Active hold/discharge/charge storage control mode. Set the charge field to enable charging and the discharge field to enable discharging. | bitfield16 |  |  | bit 0: CHARGE bit 1: DiSCHARGE
7 | 7 | 1 | RW | 0x03 0x06 0x10 | VAChaMax | Setpoint for maximum charging VA. | uint16 | VA | VAChaMax_SF
8 | 8 | 1 | RW | 0x03 0x06 0x10 | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 | % WChaMax | MinRsvPct_SF
9 | 9 | 1 | R | 0x03 | ChaState | Currently available energy as a percent of the capacity rating. | uint16 | % AhrRtg | ChaState_SF
10 | 10 | 1 | R | 0x03 | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | uint16 | AH | StorAval_SF | not supported
11 | 11 | 1 | R | 0x03 | InBatV | Internal battery voltage. | uint16 | V | InBatV_SF | not supported
12 | 12 | 1 | R | 0x03 | ChaSt | Charge status of storage device. Enumerated value. | enum16 |  |  | 1: OFF 2: EMPTY 3: DISCHAGING 4: CHARGING 5: FULL 6: HOLDING 7: TESTING The status TESTING is used during battery calibration or service charge.
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutWRte | Percent of max discharge rate. Additional Fronius description: Defines maximum Discharge rate. If not used than the default is 100 and WChaMax defines max. Discharge rate. See WChaMax for details | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
14 | 14 | 1 | RW | 0x03 0x06 0x10 | InWRte | Percent of max charging rate. Additional Fronius description: Defines maximum Charge rate. If not used than the default is 100 and WChaMax defines max. Charge rate. See WChaMax for details | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will result in a modbus exception 3 (ILLEGAL DATA VALUE). Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
15 | 15 | 1 | R | 0x03 | InOutWRte_WinTms | Time window for charge/discharge rate change. | uint16 | Secs |  | not supported
16 | 16 | 1 | RW | 0x03 0x06 0x10 | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | uint16 | Secs |  | 0 - 28800
17 | 17 | 1 | R | 0x03 | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | not supported
18 | 18 | 1 | RW | 0x03 0x06 0x10 | ChaGriSet |  | enum16 |  |  | 0: PV (Charging from grid disabled) 1: GRID (Charging from grid enabled)
19 | 19 | 1 | R | 0x03 | WChaMax_SF | Scale factor for maximum charge. | sunssf |  |  | 0
20 | 20 | 1 | R | 0x03 | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | sunssf |  |  | 0
21 | 21 | 1 | R | 0x03 | VAChaMax_SF | Scale factor for maximum charging VA. | sunssf |  |  | not supported
22 | 22 | 1 | R | 0x03 | MinRsvPct_SF | Scale factor for minimum reserve percentage. | sunssf |  |  | -2
23 | 23 | 1 | R | 0x03 | ChaState_SF | Scale factor for available energy percent. | sunssf |  |  | -2
24 | 24 | 1 | R | 0x03 | StorAval_SF | Scale factor for state of charge. | sunssf |  |  | not supported
25 | 25 | 1 | R | 0x03 | InBatV_SF | Scale factor for battery voltage. | sunssf |  |  | not supported
26 | 26 | 1 | R | 0x03 | InOutWRte_SF | Scale factor for percent charge/discharge rate. | sunssf |  |  | -2

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0