## Complete Map
Smart Meter Register Map with Integer+SF AC-Meter Model
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Smart Meter Manufacturer | string |  |  | e.g. "Fronius"
40021 | 40036 | 16 | R | 0x03 | Md | Smart Meter Model | string |  |  | e.g. "Smart Meter 63A"
40037 | 40044 | 8 | R | 0x03 | Opt | Smart Meter Name | string |  |  | e.g. "<primary>"
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of | string |  |  | e.g. "2.9"
40053 | 40068 | 16 | R | 0x03 | SN | Smart Meter Serialnumber | string |  |  | e.g. "18370117"
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model ac_meter (20x) | uint16 |  |  | 201: Single Phase (AN or AB), 202: Split Single Phase (ABN), 203: WYE-Connect Three Phase (ABCN), 204: Delta-Connect Three Phase (ABC)
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model ac_meter (20x) | uint16 | Registers |  | 105
40072 | 40072 | 1 | R | 0x03 | A | Total AC Current | int16 | A | A_SF
40073 | 40073 | 1 | R | 0x03 | AphA | Phase A Current | int16 | A | A_SF
40074 | 40074 | 1 | R | 0x03 | AphB | Phase B Current | int16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40075 | 40075 | 1 | R | 0x03 | AphC | Phase C Current | int16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40076 | 40076 | 1 | R | 0x03 | A_SF | Current scale factor | sunssf |  |  | auto-scaled on A, AphA, AphB and AphC
40077 | 40077 | 1 | R | 0x03 | PhV | Line to Neutral AC Voltage (average of active phases) | int16 | V | V_SF
40078 | 40078 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | int16 | V | V_SF
40079 | 40079 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40080 | 40080 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40081 | 40081 | 1 | R | 0x03 | PPV | Line to Line AC Voltage (average of active phases) | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40082 | 40082 | 1 | R | 0x03 | PhVphAB | Phase Voltage AB | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40083 | 40083 | 1 | R | 0x03 | PhVphBC | Phase Voltage BC | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40084 | 40084 | 1 | R | 0x03 | PhVphCA | Phase Voltage CA | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40085 | 40085 | 1 | R | 0x03 | V_SF | Voltage scale factor | sunssf |  |  | -1
40086 | 40086 | 1 | R | 0x03 | Hz | Frequency | int16 | Hz | Hz_SF
40087 | 40087 | 1 | R | 0x03 | Hz_SF | Frequency scale factor | sunssf |  |  | -2
40088 | 40088 | 1 | R | 0x03 | W | Total Real Power | int16 | W | W_SF
40089 | 40089 | 1 | R | 0x03 | WphA | Watts phase A | int16 | W | W_SF
40090 | 40090 | 1 | R | 0x03 | WphB | Watts phase B | int16 | W | W_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40091 | 40091 | 1 | R | 0x03 | WphC | Watts phase C | int16 | W | W_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40092 | 40092 | 1 | R | 0x03 | W_SF | Real Power scale factor | sunssf |  |  | auto-scaled on W, WphA, WphB and WphC
40093 | 40093 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
40094 | 40094 | 1 | R | 0x03 | VAphA | VA phase A | int16 | VA | VA_SF
40095 | 40095 | 1 | R | 0x03 | VAphB | VA phase B | int16 | VA | VA_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40096 | 40096 | 1 | R | 0x03 | VAphC | VA phase C | int16 | VA | VA_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40097 | 40097 | 1 | R | 0x03 | VA_SF | Apparent Power scale factor | sunssf |  |  | auto-scaled on VA, VAphA, VAphB and VAphC
40098 | 40098 | 1 | R | 0x03 | VAR | Reactive Power | int16 | var | VAR_SF
40099 | 40099 | 1 | R | 0x03 | VARphA | VAR phase A | int16 | var | VAR_SF
40100 | 40100 | 1 | R | 0x03 | VARphB | VAR phase B | int16 | var | VAR_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40101 | 40101 | 1 | R | 0x03 | VARphC | VAR phase C | int16 | var | VAR_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40102 | 40102 | 1 | R | 0x03 | VAR_SF | Reactive Power scale factor | sunssf |  |  | auto-scaled on VAR, VARphA, VARphB and VARphC
40103 | 40103 | 1 | R | 0x03 | PF | Power Factor | int16 | Pct | PF_SF
40104 | 40104 | 1 | R | 0x03 | PFphA | PF phase A | int16 | Pct | PF_SF
40105 | 40105 | 1 | R | 0x03 | PFphB | PF phase B | int16 | Pct | PF_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40106 | 40106 | 1 | R | 0x03 | PFphC | PF phase C | int16 | Pct | PF_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40107 | 40107 | 1 | R | 0x03 | PF_SF | Power Factor scale factor | sunssf |  |  | -1
40108 | 40109 | 2 | R | 0x03 | TotWhExp | Total Real Energy Exported | acc32 | Wh | TotWh_SF
40110 | 40111 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40112 | 40113 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40114 | 40115 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40116 | 40117 | 2 | R | 0x03 | TotWhImp | Total Real Energy Imported | acc32 | Wh | TotWh_SF
40118 | 40119 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40120 | 40121 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40122 | 40123 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40124 | 40124 | 1 | R | 0x03 | TotWh_SF | Real Energy scale factor | sunssf |  |  | auto-scaled on group `TotWh*`
40125 | 40126 | 2 | R | 0x03 | TotVAhExp | Total Apparent Energy Exported | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40127 | 40128 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40129 | 40130 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40131 | 40132 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40133 | 40134 | 2 | R | 0x03 | TotVAhImp | Total Apparent Energy Imported | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40135 | 40136 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40137 | 40138 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40139 | 40140 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
40141 | 40141 | 1 | R | 0x03 | TotVAh_SF | Apparent Energy scale factor | sunssf |  |  | auto-scaled on group `TotVAh*`
40142 | 40143 | 2 | R | 0x03 | TotVArhImpQ1 | Total Reactive Energy Imported Quadrant 1 | acc32 | varh | TotVArh_SF | not supported
40144 | 40145 | 2 | R | 0x03 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | acc32 | varh | TotVArh_SF | not supported
40146 | 40147 | 2 | R | 0x03 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | acc32 | varh | TotVArh_SF | not supported
40148 | 40149 | 2 | R | 0x03 | TotVArhImpQ1PhC | Total VAr-hours Imported Q1 phase C | acc32 | varh | TotVArh_SF | not supported
40150 | 40151 | 2 | R | 0x03 | TotVArhImpQ2 | Total Reactive Power Imported Quadrant 2 | acc32 | varh | TotVArh_SF | not supported
40152 | 40153 | 2 | R | 0x03 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | acc32 | varh | TotVArh_SF | not supported
40154 | 40155 | 2 | R | 0x03 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | acc32 | varh | TotVArh_SF | not supported
40156 | 40157 | 2 | R | 0x03 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | acc32 | varh | TotVArh_SF | not supported
40158 | 40159 | 2 | R | 0x03 | TotVArhExpQ3 | Total Reactive Power Exported Quadrant 3 | acc32 | varh | TotVArh_SF | not supported
40160 | 40161 | 2 | R | 0x03 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | acc32 | varh | TotVArh_SF | not supported
40162 | 40163 | 2 | R | 0x03 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | acc32 | varh | TotVArh_SF | not supported
40164 | 40165 | 2 | R | 0x03 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | acc32 | varh | TotVArh_SF | not supported
40166 | 40167 | 2 | R | 0x03 | TotVArhExpQ4 | Total Reactive Power Exported Quadrant 4 | acc32 | varh | TotVArh_SF | not supported
40168 | 40169 | 2 | R | 0x03 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | acc32 | varh | TotVArh_SF | not supported
40170 | 40171 | 2 | R | 0x03 | TotVArhExpQ4PhB | Total VAr-hours Exported Q4 Imported phase B | acc32 | varh | TotVArh_SF | not supported
40172 | 40173 | 2 | R | 0x03 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | acc32 | varh | TotVArh_SF | not supported
40174 | 40174 | 1 | R | 0x03 | TotVArh_SF | Reactive Energy scale factor | sunssf |  |  | not supported
40175 | 40176 | 2 | R | 0x03 | Evt | Meter Event Flags | bitfield32 |  |  | currently hardcoded to zero
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40177 | 40177 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40178 | 40178 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Smart Meter Manufacturer | string |  |  | e.g. "Fronius"
19 | 34 | 16 | R | 0x03 | Md | Smart Meter Model | string |  |  | e.g. "Smart Meter 63A"
35 | 42 | 8 | R | 0x03 | Opt | Smart Meter Name | string |  |  | e.g. "<primary>"
43 | 50 | 8 | R | 0x03 | Vr | SW version of | string |  |  | e.g. "2.9"
51 | 66 | 16 | R | 0x03 | SN | Smart Meter Serialnumber | string |  |  | e.g. "18370117"
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## ac_meter (20x)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model ac_meter (20x) | uint16 |  |  | 201: Single Phase (AN or AB), 202: Split Single Phase (ABN), 203: WYE-Connect Three Phase (ABCN), 204: Delta-Connect Three Phase (ABC)
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model ac_meter (20x) | uint16 | Registers |  | 105
3 | 3 | 1 | R | 0x03 | A | Total AC Current | int16 | A | A_SF
4 | 4 | 1 | R | 0x03 | AphA | Phase A Current | int16 | A | A_SF
5 | 5 | 1 | R | 0x03 | AphB | Phase B Current | int16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
6 | 6 | 1 | R | 0x03 | AphC | Phase C Current | int16 | A | A_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
7 | 7 | 1 | R | 0x03 | A_SF | Current scale factor | sunssf |  |  | auto-scaled on A, AphA, AphB and AphC
8 | 8 | 1 | R | 0x03 | PhV | Line to Neutral AC Voltage (average of active phases) | int16 | V | V_SF
9 | 9 | 1 | R | 0x03 | PhVphA | Phase Voltage AN | int16 | V | V_SF
10 | 10 | 1 | R | 0x03 | PhVphB | Phase Voltage BN | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
11 | 11 | 1 | R | 0x03 | PhVphC | Phase Voltage CN | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
12 | 12 | 1 | R | 0x03 | PPV | Line to Line AC Voltage (average of active phases) | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
13 | 13 | 1 | R | 0x03 | PhVphAB | Phase Voltage AB | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
14 | 14 | 1 | R | 0x03 | PhVphBC | Phase Voltage BC | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
15 | 15 | 1 | R | 0x03 | PhVphCA | Phase Voltage CA | int16 | V | V_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
16 | 16 | 1 | R | 0x03 | V_SF | Voltage scale factor | sunssf |  |  | -1
17 | 17 | 1 | R | 0x03 | Hz | Frequency | int16 | Hz | Hz_SF
18 | 18 | 1 | R | 0x03 | Hz_SF | Frequency scale factor | sunssf |  |  | -2
19 | 19 | 1 | R | 0x03 | W | Total Real Power | int16 | W | W_SF
20 | 20 | 1 | R | 0x03 | WphA | Watts phase A | int16 | W | W_SF
21 | 21 | 1 | R | 0x03 | WphB | Watts phase B | int16 | W | W_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
22 | 22 | 1 | R | 0x03 | WphC | Watts phase C | int16 | W | W_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
23 | 23 | 1 | R | 0x03 | W_SF | Real Power scale factor | sunssf |  |  | auto-scaled on W, WphA, WphB and WphC
24 | 24 | 1 | R | 0x03 | VA | AC Apparent Power | int16 | VA | VA_SF
25 | 25 | 1 | R | 0x03 | VAphA | VA phase A | int16 | VA | VA_SF
26 | 26 | 1 | R | 0x03 | VAphB | VA phase B | int16 | VA | VA_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
27 | 27 | 1 | R | 0x03 | VAphC | VA phase C | int16 | VA | VA_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
28 | 28 | 1 | R | 0x03 | VA_SF | Apparent Power scale factor | sunssf |  |  | auto-scaled on VA, VAphA, VAphB and VAphC
29 | 29 | 1 | R | 0x03 | VAR | Reactive Power | int16 | var | VAR_SF
30 | 30 | 1 | R | 0x03 | VARphA | VAR phase A | int16 | var | VAR_SF
31 | 31 | 1 | R | 0x03 | VARphB | VAR phase B | int16 | var | VAR_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
32 | 32 | 1 | R | 0x03 | VARphC | VAR phase C | int16 | var | VAR_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
33 | 33 | 1 | R | 0x03 | VAR_SF | Reactive Power scale factor | sunssf |  |  | auto-scaled on VAR, VARphA, VARphB and VARphC
34 | 34 | 1 | R | 0x03 | PF | Power Factor | int16 | Pct | PF_SF
35 | 35 | 1 | R | 0x03 | PFphA | PF phase A | int16 | Pct | PF_SF
36 | 36 | 1 | R | 0x03 | PFphB | PF phase B | int16 | Pct | PF_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
37 | 37 | 1 | R | 0x03 | PFphC | PF phase C | int16 | Pct | PF_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
38 | 38 | 1 | R | 0x03 | PF_SF | Power Factor scale factor | sunssf |  |  | -1
39 | 40 | 2 | R | 0x03 | TotWhExp | Total Real Energy Exported | acc32 | Wh | TotWh_SF
41 | 42 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
43 | 44 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
45 | 46 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
47 | 48 | 2 | R | 0x03 | TotWhImp | Total Real Energy Imported | acc32 | Wh | TotWh_SF
49 | 50 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
51 | 52 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
53 | 54 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | acc32 | Wh | TotWh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
55 | 55 | 1 | R | 0x03 | TotWh_SF | Real Energy scale factor | sunssf |  |  | auto-scaled on group `TotWh*`
56 | 57 | 2 | R | 0x03 | TotVAhExp | Total Apparent Energy Exported | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
58 | 59 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
60 | 61 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
62 | 63 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
64 | 65 | 2 | R | 0x03 | TotVAhImp | Total Apparent Energy Imported | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
66 | 67 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
68 | 69 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
70 | 71 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | acc32 | VAh | TotVAh_SF | This data-point is supported/not-supported depending on the grid connection and/or used smart meter.
72 | 72 | 1 | R | 0x03 | TotVAh_SF | Apparent Energy scale factor | sunssf |  |  | auto-scaled on group `TotVAh*`
73 | 74 | 2 | R | 0x03 | TotVArhImpQ1 | Total Reactive Energy Imported Quadrant 1 | acc32 | varh | TotVArh_SF | not supported
75 | 76 | 2 | R | 0x03 | TotVArhImpQ1PhA | Total VAr-hours Imported Q1 phase A | acc32 | varh | TotVArh_SF | not supported
77 | 78 | 2 | R | 0x03 | TotVArhImpQ1PhB | Total VAr-hours Imported Q1 phase B | acc32 | varh | TotVArh_SF | not supported
79 | 80 | 2 | R | 0x03 | TotVArhImpQ1PhC | Total VAr-hours Imported Q1 phase C | acc32 | varh | TotVArh_SF | not supported
81 | 82 | 2 | R | 0x03 | TotVArhImpQ2 | Total Reactive Power Imported Quadrant 2 | acc32 | varh | TotVArh_SF | not supported
83 | 84 | 2 | R | 0x03 | TotVArhImpQ2PhA | Total VAr-hours Imported Q2 phase A | acc32 | varh | TotVArh_SF | not supported
85 | 86 | 2 | R | 0x03 | TotVArhImpQ2PhB | Total VAr-hours Imported Q2 phase B | acc32 | varh | TotVArh_SF | not supported
87 | 88 | 2 | R | 0x03 | TotVArhImpQ2PhC | Total VAr-hours Imported Q2 phase C | acc32 | varh | TotVArh_SF | not supported
89 | 90 | 2 | R | 0x03 | TotVArhExpQ3 | Total Reactive Power Exported Quadrant 3 | acc32 | varh | TotVArh_SF | not supported
91 | 92 | 2 | R | 0x03 | TotVArhExpQ3PhA | Total VAr-hours Exported Q3 phase A | acc32 | varh | TotVArh_SF | not supported
93 | 94 | 2 | R | 0x03 | TotVArhExpQ3PhB | Total VAr-hours Exported Q3 phase B | acc32 | varh | TotVArh_SF | not supported
95 | 96 | 2 | R | 0x03 | TotVArhExpQ3PhC | Total VAr-hours Exported Q3 phase C | acc32 | varh | TotVArh_SF | not supported
97 | 98 | 2 | R | 0x03 | TotVArhExpQ4 | Total Reactive Power Exported Quadrant 4 | acc32 | varh | TotVArh_SF | not supported
99 | 100 | 2 | R | 0x03 | TotVArhExpQ4PhA | Total VAr-hours Exported Q4 Imported phase A | acc32 | varh | TotVArh_SF | not supported
101 | 102 | 2 | R | 0x03 | TotVArhExpQ4PhB | Total VAr-hours Exported Q4 Imported phase B | acc32 | varh | TotVArh_SF | not supported
103 | 104 | 2 | R | 0x03 | TotVArhExpQ4PhC | Total VAr-hours Exported Q4 Imported phase C | acc32 | varh | TotVArh_SF | not supported
105 | 105 | 1 | R | 0x03 | TotVArh_SF | Reactive Energy scale factor | sunssf |  |  | not supported
106 | 107 | 2 | R | 0x03 | Evt | Meter Event Flags | bitfield32 |  |  | currently hardcoded to zero

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0