## Index
Index
St | SunSpec Status register of the inverter model
StVnd | Fronius Status register of the inverter model (recommended to read out instead of St)
Evt1 | First SunSpec Event Flag register of the inverter model. Second one not in use, shows only zeroes.
Evt1-4 All | Fronius Event Flag registers 1 to 4 of the inverter model. Lists all state codes of all supported inverters (including IG, Agilo, CL).
Evt1-4 Galvo | Fronius Event Flag registers 1 to 4 of the inverter model. Lists all state codes of Galvo inverter family.
Evt1-4 Symo | Fronius Event Flag registers 1 to 4 of the inverter model. Lists all state codes of Symo inverter family.
Evt1-4 Primo | Fronius Event Flag registers 1 to 4 of the inverter model. Lists all state codes of Primo inverter family.
Evt1-4 IGPlus | Fronius Event Flag registers 1 to 4 of the inverter model. Lists all state codes of IG Plus inverter family.
Galvo State Codes | List of Galvo state codes that are shown in the Fronius Event Flag registers.
Symo State Codes | List of Symo state codes that are shown in the Fronius Event Flag registers.
Primo State Codes | List of Primo state codes that are shown in the Fronius Event Flag registers.
IGPlus State Codes | List of IG Plus state codes that are shown in the Fronius Event Flag registers.

## St
St (hex) | St (dec) | Name | Description | Supported?
1 | 1 | I_STATUS_OFF | Off | yes
2 | 2 | I_STATUS_SLEEPING | Sleeping (auto-shutdown) | no
3 | 3 | I_STATUS_STARTING | Starting up | yes
4 | 4 | I_STATUS_MPPT | Tracking power point | yes
5 | 5 | I_STATUS_THROTTLED | Forced power reduction | yes
6 | 6 | I_STATUS_SHUTTING_DOWN | Shutting down | no
7 | 7 | I_STATUS_FAULT | One or more faults exist | yes
8 | 8 | I_STATUS_STANDBY | Standby (service on unit)*might be in Events | yes

## StVnd
StVnd (hex) | StVnd (dec) | Name | Description | Supported?
1 | 1 | I_STATUS_OFF | Off | yes
2 | 2 | I_STATUS_SLEEPING | Sleeping (auto-shutdown) | no
3 | 3 | I_STATUS_STARTING | Starting up | yes
4 | 4 | I_STATUS_MPPT | Tracking power point | yes
5 | 5 | I_STATUS_THROTTLED | Forced power reduction | yes
6 | 6 | I_STATUS_SHUTTING_DOWN | Shutting down | no
7 | 7 | I_STATUS_FAULT | One or more faults exist | yes
8 | 8 | I_STATUS_STANDBY | Standby (service on unit)*might be in Events | yes
9 | 9 | I_STATUS_NO_BUSINIT | No SolarNet communication | yes
A | 10 | I_STATUS_NO_COMM_INV | No communication with inverter | yes
B | 11 | I_STATUS_SN_OVERCURRENT | Overcurrent on SolarNet plug detected | yes
C | 12 | I_STATUS_BOOTLOAD | Inverter is being updated | yes
D | 13 | I_STATUS_AFCI | AFCI Event | yes

## Evt1
Evt1 (hex) | Evt1 (dec) | State Codes | State | Name
1 | 1 | 471;472;474;475;494;502 | Ground fault | I_EVENT_GROUND_FAULT
2 | 2 | 309;313 | DC over voltage | I_EVENT_DC_OVER_VOLT
4 | 4 | 107;117;127;137 | AC disconnect open | I_EVENT_AC_DISCONNECT
8 | 8 |  | DC disconnect open | I_EVENT_DC_DISCONNECT
10 | 16 |  | Grid shutdown | I_EVENT_GRID_DISCONNECT
20 | 32 |  | Cabinet open | I_EVENT_CABINET_OPEN
40 | 64 |  | Manual shutdown | I_EVENT_MANUAL_SHUTDOWN
80 | 128 | 303;304;531 | Over temperature | I_EVENT_OVER_TEMP
100 | 256 | 104;105;115;125;135;203;204 | Frequency above limit | I_EVENT_OVER_FREQUENCY | *)
200 | 512 | 104;106;116;126;136;203;204 | Frequency under limit | I_EVENT_UNDER_FREQUENCY | *)
400 | 1024 | 101;102;112;122;132;201;202 | AC voltage above limit | I_EVENT_AC_OVER_VOLT | *)
800 | 2048 | 101;103;113;123;133;201;202 | AC voltage under limit | I_EVENT_AC_UNDER_VOLT | *)
1000 | 4096 | 550;551 | Blown string fuse | I_EVENT_BLOWN_STRING_FUSE
2000 | 8192 |  | Under temperature | I_EVENT_UNDER_TEMP
4000 | 16384 | 401;402;403;404;405;414;416;417;419;421;425;431;451;452;453;454;460;461;464;465;466;467;476;477;490;491;504;505;506;507;508;510;511;514;516;517;519;541;553;558;711;712;713;714;715;716;721;722;723;724;725;726;727;728;729;730;799 | Generic Memory or Communication error (internal) | I_EVENT_MEMORY_LOSS
8000 | 32768 | 245;406;407;457;469;478;515;532;533;535;555 | Hardware test failure | I_EVENT_HW_TEST_FAILURE
*) The following state codes trigger two event flags at the same time: 101, 104, 201, 202, 203 and 204. Apart from the values listed above, the values 768 (256 + 512 = 0x100 ¦ 0x200 = 0x300) and 3072 (1024 + 2048 = 0x400 ¦ 0x800 = 0xC00) are also possible.

## EvtVnd1-4 All
Event Flags 1 (hex) | Event Flags 2 (hex) | Event Flags 3 (hex) | Event Flags 4 (hex) | Event Flags 1 (dec) | Event Flags 2 (dec) | Event Flags 3 (dec) | Event Flags 4 (dec) | StateCodes | Error Class | Name
1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 447;459;474;475;502 | DC Insulation fault | INSULATION_FAULT
2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 101;104;107;108;109;117;127;137;205;206;305 | Grid error | GRID_ERROR
4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 301;321 | Overcurrent AC | AC_OVERCURRENT
8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 302 | Overcurrent DC | DC_OVERCURRENT
10 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 303;304;322 | Over-temperature | OVER_TEMP
20 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 306 | Power low | POWER_LOW
40 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 307;310;522;523 | DC low | DC_LOW
80 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 308;426 | Intermediate circuit error | INTERMEDIATE_FAULT
100 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 105;115;125;135;203 | AC frequency too high | FREQUENCY_HIGH
200 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 106;116;126;136;204 | AC frequency too low | FREQUENCY_LOW
400 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 102;112;122;132;201 | AC voltage too high | AC_VOLTAGE_HIGH
800 | 0 | 0 | 0 | 2048 | 0 | 0 | 0 | 103;113;123;133;202 | AC voltage too low | AC_VOLTAGE_LOW
1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 0 | 408 | Direct current feed in | DIRECT_CURRENT
2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 0 | 207;208;457 | Relay problem | RELAY_FAULT
4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 417;419;421;427;428;429;431;432;433;436;437;438;439;442;445;450;462;512;513;514;516;553 | Internal power stage error | POWER_STAGE_FAULT
8000 | 0 | 0 | 0 | 32768 | 0 | 0 | 0 | 409;413 | Control problems | CONTROL_FAULT
10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 0 | 453 | Guard Controller - AC voltage error | GC_GRID_VOLT_ERR
20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 0 | 454 | Guard Controller - AC Frequency Error | GC_GRID_FREQU_ERR
40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 0 | 443 | Energy transfer not possible | ENERGY_TRANSFER_FAULT
80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 0 | 455 | Reference power source AC outside tolerances | REF_POWER_SOURCE_AC
100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 0 | 456 | Error during anti islanding test | ANTI_ISLANDING_FAULT
200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 0 | 412 | Fixed voltage lower than current MPP voltage | FIXED_VOLTAGE_FAULT
400000 | 0 | 0 | 0 | 4194304 | 0 | 0 | 0 | 403;414;451;505;506;507;510;511;711;712;713;714;715;716;721;722;723;724;725;726;727;728;729;730 | Memory fault | MEMORY_FAULT
800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 0 | 464;465;466;467 | Display | DISPLAY_FAULT
1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 0 | 401;402;416;425;452;490;491;519;799 | Internal communication error | COMMUNICATION_FAULT
2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 | 0 | 406;407;487;532;533 | Temperature sensors defective | TEMP_SENSORS_FAULT
4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 0 | 460;461;518 | DC or AC board fault | DC_AC_BOARD_FAULT
8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 | 0 | 248;404;405;415 | ENS error | ENS_FAULT
10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 | 0 | 530;531;534;535;536;537;540;541;555;557 | Fan error | FAN_FAULT
20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 0 | 471;472;551 | Defective fuse | DEFECTIVE_FUSE
40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 0 | 469 | Output choke connected to wrong poles | OUTPUT_CHOKE_FAULT
80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 | 0 | 470 | The buck converter relay does not open at high DC voltage | CONVERTER_RELAY_FAULT
0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 504 | No SolarNet communication | NO_SOLARNET_COMM
0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 508 | Inverter address incorrect | INV_ADDRESS_FAULT
0 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 509 | 24h no feed in | NO_FEED_IN_24H
0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 410;515 | Faulty plug connections | PLUG_FAULT
0 | 10 | 0 | 0 | 0 | 16 | 0 | 0 | 473 | Incorrect phase allocation | PHASE_ALLOC_FAULT
0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 210 | Grid conductor open or supply phase has failed | GRID_CONDUCTOR_OPEN
0 | 40 | 0 | 0 | 0 | 64 | 0 | 0 | 558 | Incompatible or old software | SOFTWARE_ISSUE
0 | 80 | 0 | 0 | 0 | 128 | 0 | 0 | 517 | Power Derating Due To Overtemperature | POWER_DERATING
0 | 100 | 0 | 0 | 0 | 256 | 0 | 0 | 550 | Jumper set incorrectly | JUMPER_INCORRECT
0 | 200 | 0 | 0 | 0 | 512 | 0 | 0 | 559 | Incompatible feature | INCOMPATIBLE_FEATURE
0 | 400 | 0 | 0 | 0 | 1024 | 0 | 0 | 501 | Defective ventilator/air vents blocked | VENTS_BLOCKED
0 | 800 | 0 | 0 | 0 | 2048 | 0 | 0 | 560;561 | Power reduction on error | POWER_REDUCTION_ERROR
0 | 1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 240 | Arc Detected | ARC_DETECTED
0 | 2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 245 | AFCI Self Test Failed | AFCI_SELF_TEST_FAILED
0 | 4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 247 | Current Sensor Error | CURRENT_SENSOR_ERROR
0 | 8000 | 0 | 0 | 0 | 32768 | 0 | 0 | 492;493 | DC switch fault | DC_SWITCH_FAULT
0 | 10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 249 | AFCI Defective | AFCI_DEFECTIVE
0 | 20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 250 | AFCI Manual Test Successful | AFCI_MANUAL_TEST_OK
0 | 40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 476 | Power Stack Supply Missing | PS_PWR_SUPPLY_ISSUE
0 | 80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 477 | AFCI Communication Stopped | AFCI_NO_COMM
0 | 100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 478 | AFCI Manual Test Failed | AFCI_MANUAL_TEST_FAILED
0 | 200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 463 | AC polarity reversed | AC_POLARITY_REVERSED
0 | 400000 | 0 | 0 | 0 | 4194304 | 0 | 0 | 488 | AC measurement device fault | FAULTY_AC_DEVICE
0 | 800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 781;782;783;784;785;786;787;788;789;790;791;792;793;794 | Flash fault | FLASH_FAULT
0 | 1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 772;773;775;776 | General error | GENERAL_ERROR
0 | 2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 | 494 | Grounding fault | GROUNDING_ISSUE
0 | 4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 761;762;763;764;765;766;767;768 | Power limitation fault | LIMITATION_FAULT
0 | 8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 | 486 | External NO contact open | OPEN_CONTACT
0 | 10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 | 597;598;599 | External overvoltage protection has tripped | OVERVOLTAGE_PROTECTION
0 | 20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 707;708;709;710;1000-1299 | Internal processor program status | PROGRAM_STATUS
0 | 40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 701;702;703;704;705;706 | SolarNet issue | SOLARNET_ISSUE
0 | 80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 | 495;496;497;498;499 | Supply voltage fault | SUPPLY_VOLTAGE_FAULT
0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 751;752;753;754;755;756;757;758;760 | Time error | TIME_FAULT
0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 731;732;733;734;735;736;737;738;739;740;741;743;744;745;746;747;748;749;750 | USB error | USB_FAULT
0 | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 309;313 | DC high | DC_HIGH
0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 482 | Init error | INIT_ERROR

## EvtVnd1-4 Galvo
Event Flags 1 (hex) | Event Flags 2 (hex) | Event Flags 3 (hex) | Event Flags 4 (hex) | Event Flags 1 (dec) | Event Flags 2 (dec) | Event Flags 3 (dec) | Event Flags 4 (dec) | State Codes | Error Class | Name
1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 459;475;502 | DC Insulation fault | INSULATION_FAULT
2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 107;108 | Grid error | GRID_ERROR
4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 301 | Overcurrent AC | AC_OVERCURRENT
8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 302 | Overcurrent DC | DC_OVERCURRENT
10 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 303;304 | Over-temperature | OVER_TEMP
20 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 306 | Power low | POWER_LOW
40 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 307 | DC low | DC_LOW
80 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 308 | Intermediate circuit error | INTERMEDIATE_FAULT
100 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 105 | AC frequency too high | FREQUENCY_HIGH
200 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 106 | AC frequency too low | FREQUENCY_LOW
400 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 102 | AC voltage too high | AC_VOLTAGE_HIGH
800 | 0 | 0 | 0 | 2048 | 0 | 0 | 0 | 103 | AC voltage too low | AC_VOLTAGE_LOW
1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 0 | 408 | Direct current feed in | DIRECT_CURRENT
2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 0 | 457 | Relay problem | RELAY_FAULT
4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 |  | Internal power stage error | POWER_STAGE_FAULT
8000 | 0 | 0 | 0 | 32768 | 0 | 0 | 0 |  | Control problems | CONTROL_FAULT
10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 0 | 453 | Guard Controller - AC voltage error | GC_GRID_VOLT_ERR
20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 0 | 454 | Guard Controller - AC Frequency Error | GC_GRID_FREQU_ERR
40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 0 |  | Energy transfer not possible | ENERGY_TRANSFER_FAULT
80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 0 |  | Reference power source AC outside tolerances | REF_POWER_SOURCE_AC
100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 0 |  | Error during anti islanding test | ANTI_ISLANDING_FAULT
200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 0 | 412 | Fixed voltage lower than current MPP voltage | FIXED_VOLTAGE_FAULT
400000 | 0 | 0 | 0 | 4194304 | 0 | 0 | 0 | 721 | Memory fault | MEMORY_FAULT
800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 0 |  | Display | DISPLAY_FAULT
1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 0 | 401;416;425;452 | Internal communication error | COMMUNICATION_FAULT
2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 | 0 | 406;407 | Temperature sensors defective | TEMP_SENSORS_FAULT
4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 0 | 460 | DC or AC board fault | DC_AC_BOARD_FAULT
8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 | 0 | 415 | ENS error | ENS_FAULT
10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 | 0 |  | Fan error | FAN_FAULT
20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 0 | 472;551 | Defective fuse | DEFECTIVE_FUSE
40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 0 |  | Output choke connected to wrong poles | OUTPUT_CHOKE_FAULT
80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 | 0 |  | The buck converter relay does not open at high DC voltage | CONVERTER_RELAY_FAULT
0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | No SolarNet communication | NO_SOLARNET_COMM
0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 |  | Inverter address incorrect | INV_ADDRESS_FAULT
0 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 509 | 24h no feed in | NO_FEED_IN_24H
0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 |  | Faulty plug connections | PLUG_FAULT
0 | 10 | 0 | 0 | 0 | 16 | 0 | 0 |  | Incorrect phase allocation | PHASE_ALLOC_FAULT
0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 |  | Grid conductor open or supply phase has failed | GRID_CONDUCTOR_OPEN
0 | 40 | 0 | 0 | 0 | 64 | 0 | 0 | 558 | Incompatible or old software | SOFTWARE_ISSUE
0 | 80 | 0 | 0 | 0 | 128 | 0 | 0 | 517 | Power Derating Due To Overtemperature | POWER_DERATING
0 | 100 | 0 | 0 | 0 | 256 | 0 | 0 |  | Jumper set incorrectly | JUMPER_INCORRECT
0 | 200 | 0 | 0 | 0 | 512 | 0 | 0 |  | Incompatible feature | INCOMPATIBLE_FEATURE
0 | 400 | 0 | 0 | 0 | 1024 | 0 | 0 |  | Defective ventilator/air vents blocked | VENTS_BLOCKED
0 | 800 | 0 | 0 | 0 | 2048 | 0 | 0 | 560 | Power reduction on error | POWER_REDUCTION_ERROR
0 | 1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 240 | Arc Detected | ARC_DETECTED
0 | 2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 245 | AFCI Self Test Failed | AFCI_SELF_TEST_FAILED
0 | 4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 247 | Current Sensor Error | CURRENT_SENSOR_ERROR
0 | 8000 | 0 | 0 | 0 | 32768 | 0 | 0 |  | DC switch fault | DC_SWITCH_FAULT
0 | 10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 249 | AFCI Defective | AFCI_DEFECTIVE
0 | 20000 | 0 | 0 | 0 | 131072 | 0 | 0 |  | AFCI Manual Test Successful | AFCI_MANUAL_TEST_OK
0 | 40000 | 0 | 0 | 0 | 262144 | 0 | 0 |  | Power Stack Supply Missing | PS_PWR_SUPPLY_ISSUE
0 | 80000 | 0 | 0 | 0 | 524288 | 0 | 0 |  | AFCI Communication Stopped | AFCI_NO_COMM
0 | 100000 | 0 | 0 | 0 | 1048576 | 0 | 0 |  | AFCI Manual Test Failed | AFCI_MANUAL_TEST_FAILED
0 | 200000 | 0 | 0 | 0 | 2097152 | 0 | 0 |  | AC polarity reversed | AC_POLARITY_REVERSED
0 | 400000 | 0 | 0 | 0 | 4194304 | 0 | 0 |  | AC measurement device fault | FAULTY_AC_DEVICE
0 | 800000 | 0 | 0 | 0 | 8388608 | 0 | 0 |  | Flash fault | FLASH_FAULT
0 | 1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 |  | General error | GENERAL_ERROR
0 | 2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 |  | Grounding fault | GROUNDING_ISSUE
0 | 4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 766 | Power limitation fault | LIMITATION_FAULT
0 | 8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 |  | External NO contact open | OPEN_CONTACT
0 | 10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 |  | External overvoltage protection has tripped | OVERVOLTAGE_PROTECTION
0 | 20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 |  | Internal processor program status | PROGRAM_STATUS
0 | 40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 705 | SolarNet issue | SOLARNET_ISSUE
0 | 80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 |  | Supply voltage fault | SUPPLY_VOLTAGE_FAULT
0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 751;752;757;758 | Time error | TIME_FAULT
0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 731;732;733;734;735;736;738;743;745 | USB error | USB_FAULT
0 | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 309 | DC high | DC_HIGH
0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 482 | Init error | INIT_ERROR

## EvtVnd1-4 Symo
Event Flags 1 (hex) | Event Flags 2 (hex) | Event Flags 3 (hex) | Event Flags 4 (hex) | Event Flags 1 (dec) | Event Flags 2 (dec) | Event Flags 3 (dec) | Event Flags 4 (dec) | State Codes | Error Class | Name
1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 447;475;502 | DC Insulation fault | INSULATION_FAULT
2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 107;108 | Grid error | GRID_ERROR
4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 301 | Overcurrent AC | AC_OVERCURRENT
8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 302 | Overcurrent DC | DC_OVERCURRENT
10 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 303 | Over-temperature | OVER_TEMP
20 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 306 | Power low | POWER_LOW
40 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 307;522;523 | DC low | DC_LOW
80 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 308;426 | Intermediate circuit error | INTERMEDIATE_FAULT
100 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 105 | AC frequency too high | FREQUENCY_HIGH
200 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 106 | AC frequency too low | FREQUENCY_LOW
400 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 102;112 | AC voltage too high | AC_VOLTAGE_HIGH
800 | 0 | 0 | 0 | 2048 | 0 | 0 | 0 | 103 | AC voltage too low | AC_VOLTAGE_LOW
1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 0 | 408 | Direct current feed in | DIRECT_CURRENT
2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 0 | 457 | Relay problem | RELAY_FAULT
4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 417;427;431;432;436;437;438;445;450;460;461;516 | Internal power stage error | POWER_STAGE_FAULT
8000 | 0 | 0 | 0 | 32768 | 0 | 0 | 0 |  | Control problems | CONTROL_FAULT
10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 0 | 453 | Guard Controller - AC voltage error | GC_GRID_VOLT_ERR
20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 0 | 454 | Guard Controller - AC Frequency Error | GC_GRID_FREQU_ERR
40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 0 |  | Energy transfer not possible | ENERGY_TRANSFER_FAULT
80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 0 |  | Reference power source AC outside tolerances | REF_POWER_SOURCE_AC
100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 0 | 456 | Error during anti islanding test | ANTI_ISLANDING_FAULT
200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 0 | 412 | Fixed voltage lower than current MPP voltage | FIXED_VOLTAGE_FAULT
400000 | 0 | 0 | 0 | 4194304 | 0 | 0 | 0 | 451;711;712;713;714;715;721;722;723;724;725;726;727;728;729;730 | Memory fault | MEMORY_FAULT
800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 0 |  | Display | DISPLAY_FAULT
1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 0 | 401;416;425;452;519 | Internal communication error | COMMUNICATION_FAULT
2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 | 0 | 406;407 | Temperature sensors defective | TEMP_SENSORS_FAULT
4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 0 | 461 | DC or AC board fault | DC_AC_BOARD_FAULT
8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 | 0 | 415 | ENS error | ENS_FAULT
10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 | 0 |  | Fan error | FAN_FAULT
20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 0 | 472 | Defective fuse | DEFECTIVE_FUSE
40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 0 |  | Output choke connected to wrong poles | OUTPUT_CHOKE_FAULT
80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 | 0 |  | The buck converter relay does not open at high DC voltage | CONVERTER_RELAY_FAULT
0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | No SolarNet communication | NO_SOLARNET_COMM
0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 |  | Inverter address incorrect | INV_ADDRESS_FAULT
0 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 509 | 24h no feed in | NO_FEED_IN_24H
0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 |  | Faulty plug connections | PLUG_FAULT
0 | 10 | 0 | 0 | 0 | 16 | 0 | 0 |  | Incorrect phase allocation | PHASE_ALLOC_FAULT
0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 |  | Grid conductor open or supply phase has failed | GRID_CONDUCTOR_OPEN
0 | 40 | 0 | 0 | 0 | 64 | 0 | 0 | 558 | Incompatible or old software | SOFTWARE_ISSUE
0 | 80 | 0 | 0 | 0 | 128 | 0 | 0 | 517 | Power Derating Due To Overtemperature | POWER_DERATING
0 | 100 | 0 | 0 | 0 | 256 | 0 | 0 |  | Jumper set incorrectly | JUMPER_INCORRECT
0 | 200 | 0 | 0 | 0 | 512 | 0 | 0 | 559 | Incompatible feature | INCOMPATIBLE_FEATURE
0 | 400 | 0 | 0 | 0 | 1024 | 0 | 0 |  | Defective ventilator/air vents blocked | VENTS_BLOCKED
0 | 800 | 0 | 0 | 0 | 2048 | 0 | 0 | 560 | Power reduction on error | POWER_REDUCTION_ERROR
0 | 1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 240 | Arc Detected | ARC_DETECTED
0 | 2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 245 | AFCI Self Test Failed | AFCI_SELF_TEST_FAILED
0 | 4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 247 | Current Sensor Error | CURRENT_SENSOR_ERROR
0 | 8000 | 0 | 0 | 0 | 32768 | 0 | 0 |  | DC switch fault | DC_SWITCH_FAULT
0 | 10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 249 | AFCI Defective | AFCI_DEFECTIVE
0 | 20000 | 0 | 0 | 0 | 131072 | 0 | 0 |  | AFCI Manual Test Successful | AFCI_MANUAL_TEST_OK
0 | 40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 476 | Power Stack Supply Missing | PS_PWR_SUPPLY_ISSUE
0 | 80000 | 0 | 0 | 0 | 524288 | 0 | 0 |  | AFCI Communication Stopped | AFCI_NO_COMM
0 | 100000 | 0 | 0 | 0 | 1048576 | 0 | 0 |  | AFCI Manual Test Failed | AFCI_MANUAL_TEST_FAILED
0 | 200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 463 | AC polarity reversed | AC_POLARITY_REVERSED
0 | 400000 | 0 | 0 | 0 | 4194304 | 0 | 0 |  | AC measurement device fault | FAULTY_AC_DEVICE
0 | 800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 782;783;784;789;794 | Flash fault | FLASH_FAULT
0 | 1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 772;773;775 | General error | GENERAL_ERROR
0 | 2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 |  | Grounding fault | GROUNDING_ISSUE
0 | 4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 761;762;765;766;767;768 | Power limitation fault | LIMITATION_FAULT
0 | 8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 |  | External NO contact open | OPEN_CONTACT
0 | 10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 |  | External overvoltage protection has tripped | OVERVOLTAGE_PROTECTION
0 | 20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 707 | Internal processor program status | PROGRAM_STATUS
0 | 40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 701;702;703;706 | SolarNet issue | SOLARNET_ISSUE
0 | 80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 |  | Supply voltage fault | SUPPLY_VOLTAGE_FAULT
0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 751;754;755;757;758;760 | Time error | TIME_FAULT
0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 731;732;733;734;735;736;737;738;740;741;743;745;746 | USB error | USB_FAULT
0 | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 309;313 | DC high | DC_HIGH
0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 482 | Init error | INIT_ERROR

## EvtVnd1-4 Primo
Event Flags 1 (hex) | Event Flags 2 (hex) | Event Flags 3 (hex) | Event Flags 4 (hex) | Event Flags 1 (dec) | Event Flags 2 (dec) | Event Flags 3 (dec) | Event Flags 4 (dec) | State Codes | Error Class | Name
1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 447;459;474;475;502 | DC Insulation fault | INSULATION_FAULT
2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 107;108 | Grid error | GRID_ERROR
4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 301 | Overcurrent AC | AC_OVERCURRENT
8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 302 | Overcurrent DC | DC_OVERCURRENT
10 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 303;304 | Over-temperature | OVER_TEMP
20 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 306 | Power low | POWER_LOW
40 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 307 | DC low | DC_LOW
80 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 308;426 | Intermediate circuit error | INTERMEDIATE_FAULT
100 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 105 | AC frequency too high | FREQUENCY_HIGH
200 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 106 | AC frequency too low | FREQUENCY_LOW
400 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 102;112 | AC voltage too high | AC_VOLTAGE_HIGH
800 | 0 | 0 | 0 | 2048 | 0 | 0 | 0 | 103 | AC voltage too low | AC_VOLTAGE_LOW
1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 0 | 408 | Direct current feed in | DIRECT_CURRENT
2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 0 | 457 | Relay problem | RELAY_FAULT
4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 417;419;421;427;428;431;436;437;438;445;450;462;516 | Internal power stage error | POWER_STAGE_FAULT
8000 | 0 | 0 | 0 | 32768 | 0 | 0 | 0 |  | Control problems | CONTROL_FAULT
10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 0 | 453 | Guard Controller - AC voltage error | GC_GRID_VOLT_ERR
20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 0 | 454 | Guard Controller - AC Frequency Error | GC_GRID_FREQU_ERR
40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 0 | 443 | Energy transfer not possible | ENERGY_TRANSFER_FAULT
80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 0 |  | Reference power source AC outside tolerances | REF_POWER_SOURCE_AC
100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 0 | 456 | Error during anti islanding test | ANTI_ISLANDING_FAULT
200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 0 | 412 | Fixed voltage lower than current MPP voltage | FIXED_VOLTAGE_FAULT
400000 | 0 | 0 | 0 | 4194304 | 0 | 0 | 0 | 451;721 | Memory fault | MEMORY_FAULT
800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 0 |  | Display | DISPLAY_FAULT
1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 0 | 401;416;425;452 | Internal communication error | COMMUNICATION_FAULT
2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 | 0 | 406;407 | Temperature sensors defective | TEMP_SENSORS_FAULT
4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 0 | 460;461 | DC or AC board fault | DC_AC_BOARD_FAULT
8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 | 0 | 415 | ENS error | ENS_FAULT
10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 | 0 |  | Fan error | FAN_FAULT
20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 0 |  | Defective fuse | DEFECTIVE_FUSE
40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 0 |  | Output choke connected to wrong poles | OUTPUT_CHOKE_FAULT
80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 | 0 |  | The buck converter relay does not open at high DC voltage | CONVERTER_RELAY_FAULT
0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | No SolarNet communication | NO_SOLARNET_COMM
0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 |  | Inverter address incorrect | INV_ADDRESS_FAULT
0 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 509 | 24h no feed in | NO_FEED_IN_24H
0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 515 | No communication with filter | FILTER_COMM_FAULT
0 | 10 | 0 | 0 | 0 | 16 | 0 | 0 |  | Incorrect phase allocation | PHASE_ALLOC_FAULT
0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 |  | Grid conductor open or supply phase has failed | GRID_CONDUCTOR_OPEN
0 | 40 | 0 | 0 | 0 | 64 | 0 | 0 | 558 | Incompatible or old software | SOFTWARE_ISSUE
0 | 80 | 0 | 0 | 0 | 128 | 0 | 0 | 517 | Power Derating Due To Overtemperature | POWER_DERATING
0 | 100 | 0 | 0 | 0 | 256 | 0 | 0 |  | Jumper set incorrectly | JUMPER_INCORRECT
0 | 200 | 0 | 0 | 0 | 512 | 0 | 0 |  | Incompatible feature | INCOMPATIBLE_FEATURE
0 | 400 | 0 | 0 | 0 | 1024 | 0 | 0 |  | Defective ventilator/air vents blocked | VENTS_BLOCKED
0 | 800 | 0 | 0 | 0 | 2048 | 0 | 0 | 560 | Power reduction on error | POWER_REDUCTION_ERROR
0 | 1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 240 | Arc Detected | ARC_DETECTED
0 | 2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 245 | AFCI Self Test Failed | AFCI_SELF_TEST_FAILED
0 | 4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 247 | Current Sensor Error | CURRENT_SENSOR_ERROR
0 | 8000 | 0 | 0 | 0 | 32768 | 0 | 0 |  | DC switch fault | DC_SWITCH_FAULT
0 | 10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 249 | AFCI Defective | AFCI_DEFECTIVE
0 | 20000 | 0 | 0 | 0 | 131072 | 0 | 0 |  | AFCI Manual Test Successful | AFCI_MANUAL_TEST_OK
0 | 40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 476 | Power Stack Supply Missing | PS_PWR_SUPPLY_ISSUE
0 | 80000 | 0 | 0 | 0 | 524288 | 0 | 0 |  | AFCI Communication Stopped | AFCI_NO_COMM
0 | 100000 | 0 | 0 | 0 | 1048576 | 0 | 0 |  | AFCI Manual Test Failed | AFCI_MANUAL_TEST_FAILED
0 | 200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 463 | AC polarity reversed | AC_POLARITY_REVERSED
0 | 400000 | 0 | 0 | 0 | 4194304 | 0 | 0 |  | AC measurement device fault | FAULTY_AC_DEVICE
0 | 800000 | 0 | 0 | 0 | 8388608 | 0 | 0 |  | Flash fault | FLASH_FAULT
0 | 1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 |  | General error | GENERAL_ERROR
0 | 2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 |  | Grounding fault | GROUNDING_ISSUE
0 | 4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 766 | Power limitation fault | LIMITATION_FAULT
0 | 8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 |  | External NO contact open | OPEN_CONTACT
0 | 10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 |  | External overvoltage protection has tripped | OVERVOLTAGE_PROTECTION
0 | 20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 |  | Internal processor program status | PROGRAM_STATUS
0 | 40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 705 | SolarNet issue | SOLARNET_ISSUE
0 | 80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 |  | Supply voltage fault | SUPPLY_VOLTAGE_FAULT
0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 751;752;757;758 | Time error | TIME_FAULT
0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 731;732;733;734;735;736;738;743;745 | USB error | USB_FAULT
0 | 0 | 4 | 0 | 0 | 0 | 4 | 0 | 309;313 | DC high | DC_HIGH
0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 482 | Init error | INIT_ERROR

## EvtVnd1-4 IGPlus
Event Flags 1 (hex) | Event Flags 2 (hex) | Event Flags 3 (hex) | Event Flags 4 (hex) | Event Flags 1 (dec) | Event Flags 2 (dec) | Event Flags 3 (dec) | Event Flags 4 (dec) | State Codes | Error Class | Name
1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 474;475;502 | DC Insulation fault | INSULATION_FAULT
2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 107;108;109;117;127;137;305 | Grid error | GRID_ERROR
4 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 301 | Overcurrent AC | AC_OVERCURRENT
8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 302 | Overcurrent DC | DC_OVERCURRENT
10 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 303;304 | Over-temperature | OVER_TEMP
20 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 306 | Power low | POWER_LOW
40 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 307 | DC low | DC_LOW
80 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 308 | Intermediate circuit error | INTERMEDIATE_FAULT
100 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 105;115;125;135 | AC frequency too high | FREQUENCY_HIGH
200 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 106;116;126;136 | AC frequency too low | FREQUENCY_LOW
400 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 102;112;122;132 | AC voltage too high | AC_VOLTAGE_HIGH
800 | 0 | 0 | 0 | 2048 | 0 | 0 | 0 | 103;113;123;133 | AC voltage too low | AC_VOLTAGE_LOW
1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 0 | 408 | Direct current feed in | DIRECT_CURRENT
2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 0 | 207;208;457 | Relay problem | RELAY_FAULT
4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 417;419;421;431;439;442;445;450;512;513;514;516;553 | Internal power stage error | POWER_STAGE_FAULT
8000 | 0 | 0 | 0 | 32768 | 0 | 0 | 0 | 413 | Control problems | CONTROL_FAULT
10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 0 | 453 | Guard Controller - AC voltage error | GC_GRID_VOLT_ERR
20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 0 | 454 | Guard Controller - AC Frequency Error | GC_GRID_FREQU_ERR
40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 0 | 443 | Energy transfer not possible | ENERGY_TRANSFER_FAULT
80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 0 | 455 | Reference power source AC outside tolerances | REF_POWER_SOURCE_AC
100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 0 | 456 | Error during anti islanding test | ANTI_ISLANDING_FAULT
200000 | 0 | 0 | 0 | 2097152 | 0 | 0 | 0 | 412 | Fixed voltage lower than current MPP voltage | FIXED_VOLTAGE_FAULT
400000 | 0 | 0 | 0 | 4194304 | 0 | 0 | 0 | 403;414;451;505;506;507;510;511 | Memory fault | MEMORY_FAULT
800000 | 0 | 0 | 0 | 8388608 | 0 | 0 | 0 | 464;465;466;467 | Display | DISPLAY_FAULT
1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 | 0 | 401;402;416;425;452 | Internal communication error | COMMUNICATION_FAULT
2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 | 0 | 406;407 | Temperature sensors defective | TEMP_SENSORS_FAULT
4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 | 0 | 460;461 | DSP error | DSP_ERROR
8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 | 0 | 248 | ENS error | ENS_FAULT
10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 | 0 |  | Fan error | FAN_FAULT
20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 | 0 | 471;472;551 | Defective fuse | DEFECTIVE_FUSE
40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 | 0 | 469 | Output choke connected to wrong poles | OUTPUT_CHOKE_FAULT
80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 | 0 | 470 | The buck converter relay does not open at high DC voltage | CONVERTER_RELAY_FAULT
0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 504 | No SolarNet communication | NO_SOLARNET_COMM
0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 508 | Inverter address incorrect | INV_ADDRESS_FAULT
0 | 4 | 0 | 0 | 0 | 4 | 0 | 0 | 509 | 24h no feed in | NO_FEED_IN_24H
0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 515 | Faulty plug connections | PLUG_FAULT
0 | 10 | 0 | 0 | 0 | 16 | 0 | 0 |  | Incorrect phase allocation | PHASE_ALLOC_FAULT
0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 |  | Grid conductor open or supply phase has failed | GRID_CONDUCTOR_OPEN
0 | 40 | 0 | 0 | 0 | 64 | 0 | 0 | 558 | Incompatible or old software | SOFTWARE_ISSUE
0 | 80 | 0 | 0 | 0 | 128 | 0 | 0 | 517 | Change of master | MASTER_CHANGE
0 | 100 | 0 | 0 | 0 | 256 | 0 | 0 | 550 | Jumper set incorrectly | JUMPER_INCORRECT
0 | 200 | 0 | 0 | 0 | 512 | 0 | 0 | 559 | LVRT | LVRT
0 | 400 | 0 | 0 | 0 | 1024 | 0 | 0 |  | Defective ventilator/air vents blocked | VENTS_BLOCKED
0 | 800 | 0 | 0 | 0 | 2048 | 0 | 0 | 560;561 | Power reduction on error | POWER_REDUCTION_ERROR
0 | 1000 | 0 | 0 | 0 | 4096 | 0 | 0 | 240 | Arc Detected | ARC_DETECTED
0 | 2000 | 0 | 0 | 0 | 8192 | 0 | 0 | 245 | AFCI Self Test Failed | AFCI_SELF_TEST_FAILED
0 | 4000 | 0 | 0 | 0 | 16384 | 0 | 0 | 247 | Current Sensor Error | CURRENT_SENSOR_ERROR
0 | 8000 | 0 | 0 | 0 | 32768 | 0 | 0 |  | DC switch fault | DC_SWITCH_FAULT
0 | 10000 | 0 | 0 | 0 | 65536 | 0 | 0 | 249 | AFCI Defective | AFCI_DEFECTIVE
0 | 20000 | 0 | 0 | 0 | 131072 | 0 | 0 | 250 | AFCI Manual Test Successful | AFCI_MANUAL_TEST_OK
0 | 40000 | 0 | 0 | 0 | 262144 | 0 | 0 | 476 | Power Stack Supply Missing | PS_PWR_SUPPLY_ISSUE
0 | 80000 | 0 | 0 | 0 | 524288 | 0 | 0 | 477 | AFCI Communication Stopped | AFCI_NO_COMM
0 | 100000 | 0 | 0 | 0 | 1048576 | 0 | 0 | 478 | AFCI Manual Test Failed | AFCI_MANUAL_TEST_FAILED
0 | 200000 | 0 | 0 | 0 | 2097152 | 0 | 0 |  | AC polarity reversed | AC_POLARITY_REVERSED
0 | 400000 | 0 | 0 | 0 | 4194304 | 0 | 0 |  | AC measurement device fault | FAULTY_AC_DEVICE
0 | 800000 | 0 | 0 | 0 | 8388608 | 0 | 0 |  | Flash fault | FLASH_FAULT
0 | 1000000 | 0 | 0 | 0 | 16777216 | 0 | 0 |  | General error | GENERAL_ERROR
0 | 2000000 | 0 | 0 | 0 | 33554432 | 0 | 0 |  | Grounding fault | GROUNDING_ISSUE
0 | 4000000 | 0 | 0 | 0 | 67108864 | 0 | 0 |  | Power limitation fault | LIMITATION_FAULT
0 | 8000000 | 0 | 0 | 0 | 134217728 | 0 | 0 |  | External NO contact open | OPEN_CONTACT
0 | 10000000 | 0 | 0 | 0 | 268435456 | 0 | 0 |  | External overvoltage protection has tripped | OVERVOLTAGE_PROTECTION
0 | 20000000 | 0 | 0 | 0 | 536870912 | 0 | 0 |  | Internal processor program status | PROGRAM_STATUS
0 | 40000000 | 0 | 0 | 0 | 1073741824 | 0 | 0 |  | SolarNet issue | SOLARNET_ISSUE
0 | 80000000 | 0 | 0 | 0 | 2147483648 | 0 | 0 |  | Supply voltage fault | SUPPLY_VOLTAGE_FAULT
0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 |  | Time error | TIME_FAULT
0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 |  | USB error | USB_FAULT
0 | 0 | 4 | 0 | 0 | 0 | 4 | 0 |  | DC high | DC_HIGH
0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 |  | Init error | INIT_ERROR

## Galvo State Codes
102 | AC voltage too high
103 | AC voltage too low
105 | AC frequency too high
106 | AC frequency too low
107 | No AC grid detected / Wrong AC Grid State detected
108 | Islanding detected
240 | Arc Detected
245 | Arc Fault Cicruit Interrupter (AFCI) Selftest failed
247 | Arc Fault Cicruit Interrupter (AFCI) current sensor error
249 | Arc Fault Cicruit Interrupter (AFCI) detected unplausibel measurement values
301 | Overcurrent AC
302 | Overcurrent DC
303 | Channel 1 Overtemperature
304 | Channel 2 Overtemperature
306 | Power Low
307 | DC Voltage Low
308 | Intermediate circuit voltage too high
309 | DC Input Overvoltage
401 | Power Stack Communication Error
406 | Error temperature sensor on DC board
407 | Error temperature sensor on AC board
408 | DC detected in grid
412 | DC1 Fix Voltage Out Of Range
415 | Wired Shutdown Triggered
416 | RECERBO - Power Stack Communication Error
425 | Data Exchange Timeout
445 | Invalid Parameters detected
452 | Power Stack - Filter Communication Error
453 | Guard Controller - AC voltage error
454 | Guard Controller - AC Frequency Error
457 | Grid Relay Error
459 | Guard Controller - Isolation Selftest Error
460 | Power Stack / Filter Print Reference Voltage Error
472 | Ground-Fault Detector Interrupter Fuse Broken
475 | Isolation Too Low Error
482 | Installation wizard aborted
502 | Warning - Isolation Too Low
509 | No Feed In For 24 Hours
517 | Power Derating Due To Overtemperature
551 | Ground Missing
558 | Incompatible Power Stack Software
560 | Power Derating Due To High Grid Frequency
568 | Multifunction current interface Warning
668 | External I/O Error
721 | EEPROM - Reinitialized
731 | USB Flash Drive Initializing Error
732 | USB Flash Drive Overcurrent
733 | No USB Flash Drive Inserted
734 | No Software Update Found On USB Flash Drive
735 | No Supported Software Update Found On USB Flash Drive
736 | USB Flash Drive Flash Drive Read/Write Error
738 | Log-File Can't Be Created On The USB Flash Drive
743 | Software Update Failed
745 | Software Update Checksum Wrong
751 | Real Time Clock - Time Lost
752 | Real Time Clock - Hardware Error
757 | Real Time Clock - Hardware Error
758 | Real Time Clock - Emergency Mode
766 | Power Limit Not Found

## Symo State Codes
102 | AC voltage too high
103 | AC voltage too low
105 | AC frequency too high
106 | AC frequency too low
107 | No AC grid detected / Wrong AC Grid State detected
108 | Islanding detected
112 | Residual Current Detected
240 | Arc Detected
241 | Arc detection confirmation 1
242 | Arc detection confirmation 2
245 | Arc Fault Cicruit Interrupter (AFCI) Selftest failed
247 | Arc Fault Cicruit Interrupter (AFCI) current sensor error
249 | Arc Fault Cicruit Interrupter (AFCI) detected unplausibel measurement values
301 | Overcurrent AC
302 | Overcurrent DC
303 | Channel 1 Overtemperature
306 | Power Low
307 | DC Voltage Low
308 | Intermediate circuit voltage too high
309 | DC1 Input Overvoltage
313 | DC2 Input Overvoltage
406 | Error temperature sensor on DC board
407 | Error temperature sensor on AC board
408 | DC detected in grid
412 | DC1 Fix Voltage Out Of Range
415 | Wired Shutdown Triggered
416 | RECERBO - Power Stack Communication Error
417 | Hardware-ID Collision
425 | Data Exchange Timeout
426 | Intermediate Circuit Loading Timeout
427 | Power Stack Ready Timeout
431 | Power Stack In Bootmode
432 | Consistent error in power stack management
433 | Allocation error of dynamic addresses
436 | Invalid Bitmap Received
437 | Power Stack Event Handling Error
438 | Problem while error transmission from power stack to Recerbo
445 | Invalid Parameters detected
447 | Isolation Error
448 | No Neutral Wire
450 | Guard Controller - Communication Error
451 | Memory Check Error
452 | Power Stack - Filter Communication Error
453 | Guard Controller - AC voltage error
454 | Guard Controller - AC Frequency Error
456 | Guard Controller - Anti Islanding Selftest Error
457 | Grid Relay Error
458 | Residual Current Monitoring Unit (RCMU) Error
459 | Guard Controller - Isolation Selftest Error
460 | Power Stack / Filter Print Reference Voltage Error
461 | RAM Error / Collective Fault
462 | Guard Controller - DC injection into grid detected
463 | AC Poles reversed
472 | Ground-Fault Detector Interrupter Fuse Broken
474 | Residual Current Sensor defect
475 | Isolation Too Low Error
476 | Power Stack Supply Missing
480 | Incompatible feature
481 | Not supported feature
482 | Installation wizard aborted
483 | DC fix voltage out of range
484 | CAN transfer timeout
485 | CAN transmit buffer full
502 | Warning - Isolation Too Low
509 | No Feed In For 24 Hours
516 | Power Stack EEPROM Error
517 | Power Derating Due To Overtemperature
519 | Filter Board - EEPROM Error
520 | MPP Tracker #1 - No Feed In For 24 Hours
521 | MPP Tracker #2 - No Feed In For 24 Hours
522 | DC1 Input Voltage To Low
523 | DC2 Input Voltage Low
558 | Incompatible Power Stack Software
559 | Incompatible RECERBO Feature
560 | Power Derating Due To High Grid Frequency
565 | Arc Fault Cicruit Interrupter SD Card Error [US only]
566 | Arc Fault Cicruit Interrupter Deactivated Warning [US only]
567 | Grid Voltage Dependent Power Derating
701 | Solar Net - Node Type Out Of Range
702 | Solar Net - Receive Buffer Full
703 | Solar Net - Send Buffer Full
705 | Solar Net - Node Type Conflict
706 | CapKey - Get Version Failed
707 | CapKey - Update Failed
711 | EEPROM Write - Wrong Data Length
712 | EEPROM Write - Descriptor Not Found
713 | EEPROM Read - Descriptor Not Found
714 | EEPROM Read Warning - CRC Header Fail Will Retry
715 | EEPROM Read - CRC Header Fail Give It Up
721 | EEPROM - Reinitialized
722 | EEPROM - Wait Busy Timeout
723 | EEPROM Write - Verify Fail Will Retry
724 | EEPROM Write - Verify Fail Give It Up
725 | EEPROM Read - CRC Data Fail Will Retry
726 | EEPROM Read - CRC Data Fail Give It Up
727 | EEPROM Check Data Warning - All Data Corrupt
730 | EEPROM Check Data - Data Restored
731 | USB Flash Drive Initializing Error
732 | USB Flash Drive Overcurrent
733 | No USB Flash Drive Inserted
734 | No Software Update Found On USB Flash Drive
735 | No Supported Software Update Found On USB Flash Drive
736 | USB Flash Drive Flash Drive Read/Write Error
737 | Software Update Can Not Be Read From The USB Flash Drive
738 | Log-File Can't Be Created On The USB Flash Drive
740 | USB Flash Drive Enumeration Error
741 | USB Flash Drive Logging Write Error
743 | Software Update Failed
745 | Software Update Checksum Wrong
746 | Product Matrix Code (PMC) Read Error During Software Update
751 | Real Time Clock - Time Lost
752 | Real Time Clock - Hardware Error
754 | Real Time Clock - Time Set
755 | EEPROM Data Written
757 | Real Time Clock - Hardware Error
758 | Real Time Clock - Emergency Mode
760 | System Crystal Broken
761 | Device Data Unit Memory Read Error
762 | Plugged Device Data Unit Read Error
765 | Random Number Generator Error
766 | Power Limit Not Found
767 | Power Limiter Communication Error
768 | Power Limit Not Identical
772 | Memory Not Available
773 | Update Group Zero
775 | Power Stack Product Matrix Code Invalid
782 | Update Flash - CRC Error
783 | Update Flash - Header CRC Error
784 | Update Flash - Timeout
789 | Update Flash - Read Value (Header CRC Error)

## Primo State Codes
102 | AC voltage too high
103 | AC voltage too low
105 | AC frequency too high
106 | AC frequency too low
107 | No AC grid detected / Wrong AC Grid State detected
108 | Islanding detected
112 | Residual Current Detected
240 | Arc Detected
245 | Arc Fault Cicruit Interrupter (AFCI) Selftest failed
247 | Arc Fault Cicruit Interrupter (AFCI) current sensor error
249 | Arc Fault Cicruit Interrupter (AFCI) detected unplausibel measurement values
301 | Overcurrent AC
302 | Overcurrent DC
303 | Channel 1 Overtemperature
304 | Channel 2 Overtemperature
305 | Intermediate Circuit Undervoltage
306 | Power Low
307 | DC Voltage Low
308 | Intermediate circuit voltage too high
309 | DC1 Input Overvoltage
313 | DC2 Input Overvoltage
401 | Power Stack Communication Error
406 | Error temperature sensor on DC board
407 | Error temperature sensor on AC board
408 | DC detected in grid
412 | DC1 Fix Voltage Out Of Range
415 | Wired Shutdown Triggered
416 | RECERBO - Power Stack Communication Error
417 | Hardware-ID Collision
419 | Unique ID-collision
421 | Hardware ID-sequence error
425 | Data Exchange Timeout
426 | Intermediate Circuit Loading Timeout
427 | Power Stack Ready Timeout
428 | Possible hardware fault
431 | Power Stack In Bootmode
436 | Invalid Bitmap Received
437 | Power Stack Event Handling Error
438 | Functional incompatibility
443 | DC/DC energy transfer failure
445 | Invalid Parameters detected
447 | Isolation Error
450 | Guard Controller - Communication Error
451 | Memory Check Error
452 | Power Stack - Filter Communication Error
453 | Guard Controller - AC voltage error
454 | Guard Controller - AC Frequency Error
456 | Guard Controller - Anti Islanding Selftest Error
457 | Grid Relay Error
459 | Guard Controller - Isolation Selftest Error
460 | Power Stack / Filter Print Reference Voltage Error
461 | RAM Error / Collective Fault
462 | Guard Controller - DC injection into grid detected
463 | AC Poles reversed
474 | Residual Current Sensor defect
475 | Isolation Too Low Error
476 | Power Stack Supply Missing
482 | Installation wizard aborted
502 | Warning - Isolation Too Low
509 | No Feed In For 24 Hours
515 | No communication with filter
516 | Power Stack EEPROM Error
517 | Power Derating Due To Overtemperature
558 | Incompatible Power Stack Software
560 | Power Derating Due To High Grid Frequency
705 | Solar Net - Node Type Conflict
721 | EEPROM - Reinitialized
731 | USB Flash Drive Initializing Error
732 | USB Flash Drive Overcurrent
733 | No USB Flash Drive Inserted
734 | No Software Update Found On USB Flash Drive
735 | No Supported Software Update Found On USB Flash Drive
736 | USB Flash Drive Flash Drive Read/Write Error
738 | Log-File Can't Be Created On The USB Flash Drive
743 | Software Update Failed
745 | Software Update Checksum Wrong
751 | Real Time Clock - Time Lost
752 | Real Time Clock - Hardware Error
757 | Real Time Clock - Hardware Error
758 | Real Time Clock - Emergency Mode
766 | Power Limit Not Found

## IGPlus State Codes
102 | AC voltage too high
103 | AC voltage too low
105 | AC frequency too high
106 | AC frequency too low
107 | No AC grid detected
108 | Islanding detected
109 | General mains error
112 | AC voltage too high Phase 1
113 | AC voltage too low Phase 1
115 | AC frequency too high Phase 1
116 | AC frequency too low Phase 1
117 | No AC grid detected Phase 1
122 | AC voltage too high Phase 2
123 | AC voltage too low Phase 2
125 | AC frequency too high Phase 2
126 | AC frequency too low Phase 2
127 | No AC grid detected Phase 2
132 | AC voltage too high Phase 3
133 | AC voltage too low Phase 3
135 | AC frequency too high Phase 3
136 | AC frequency too low Phase 3
137 | No AC grid detected Phase 3
207 | General mains error
208 | Jumper Test Failed
240 | Arc detected
245 | Arc Blocker (PV-AFCI-NL board) self test failed
247 | Arc Blocker (PV-AFCI-NL board) current sensor error
248 | Arc Blocker (PV-AFCI-NL board) Jumper Test Failed
249 | Arc Blocker (PV-AFCI-NL board) damaged
250 | NO ERROR - Manual test of Arc Blocker (PV-AFCI-NL board) successful
301 | Overcurrent AC
302 | Overcurrent DC
303 | Overtemperature PINCI board
304 | Overtemperature Heat sink
305 | Energytransfer not possible
306 | Power Low
307 | DC Low
308 | Intermediate circuit voltage too high
401 | Communication error between IG BRAIN and PINCI board
402 | Write access to the internal memory failed
403 | Internal memory with country settings incomplete
406 | Temperature sensor PINCI board faulty
407 | Temperature sensor heat sink faulty or not connected
408 | DC injection
412 | DC voltage too high
413 | DC voltage too high
414 | Memory array for Fronius IG Plus type in EEPROM faulty
416 | Communication error between IG BRAIN and power stack
417 | Hardware ID-collision
419 | Unique ID-collision
421 | Hardware ID-sequence error
425 | Receive timeout for data exchange with one or more power stacks exceeded
431 | All PINCI boards are in boot mode
439 | Disconnection of one PINCI board because of a problem on another PINCI board (in Balance Mode)
442 | Master for one phase could not be assigned
443 | DC/DC energy transfer failure
445 | Wrong power stack configuration
450 | Guard Detection - Monitoring of the central processing unit is active
451 | Guard Memory problem
452 | Guard communication problem
453 | Guard AC voltage failure detected
454 | Guard AC frequency failure detected
455 | Guard AC failure detected
456 | Guard anti islanding test failure detected
457 | Guard mains relays stuck
460 | Referencevoltage outside permitted limits
461 | Internal memory (RAM) consitency check failure
464 | Display version incompatible
465 | Display version unkown
466 | Display not available
467 | Timeout during start up
469 | Output inductor connection mixed up
470 | Buck converter relay doesn't open
471 | Module grounding fuse defective
472 | Grounding Fuse defect
474 | 100kOhm module grounding measurement detects failure
475 | DC isolation failure
476 | Arc Blocker Communication Fail
477 | Arc Blocker Communication has stopped
478 | Arc Blocker Manual Test failed
502 | DC isolation failure
504 | Solar Net address conflict
505 | Internal memory with country settings incomplete
506 | Internal memory with TOTAL values incomplete
507 | Internal memory with DAY/YEAR values incomplete
508 | Internal memory for IG Number is incomplete
509 | No feed in operation for 24 hours
510 | Errors detected by Solar Net self diagnostic system
511 | Errors detected by Solar Net Sensor Card self diagnostic system
512 | According to the device type too many PINCI boards have been detected
513 | PINCI boards in boot mode
514 | According to the device type not enough PINCI boards have been detected
515 | One or more PINCI boards with State Codes (406/407/409/410)
516 | One PINCI board exceeds the permitted limit of error messages per day
517 | Permanent Power Low or DC Low error
550 | String fuse defective
551 | Grounding Fuse defective
553 | Communication problem with one phasemaster
558 | Feature disabled
559 | Low Voltage Ride Through (LVRT) active
560 | Grid Frequency-dependent Power Reduction (GFPR) active
561 | Power reduction because of over temperature