## Complete Map
Fronius Datamanager Register Map: IG Sensor Card (1, 302, 303, 307)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device model | String32
40037 | 40044 | 8 | R | 0x03 | Opt | Options | String16
40045 | 40052 | 8 | R | 0x03 | Vr | SW version | String16
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber | String32
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Irradiance Modbus Register Model | uint16 |  |  | 302
40071 | 40071 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 5
40072 | 40072 | 1 | R | 0x03 | GHI | Global Horizontal Irradiance | uint16 | W / m2
40073 | 40073 | 1 | R | 0x03 | POAI | Plane-of-Array Irradiance | uint16 | W / m2 |  | not supported
40074 | 40074 | 1 | R | 0x03 | DFI | Diffuse Irradiance | uint16 | W / m2 |  | not supported
40075 | 40075 | 1 | R | 0x03 | DNI | Direct Normal Irradiance | uint16 | W / m2 |  | not supported
40076 | 40076 | 1 | R | 0x03 | OTI | Other Irradiance | uint16 | W / m2 |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40077 | 40077 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Back of Module Temperature Modbus Register Model | uint16 |  |  | 303
40078 | 40078 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 2 (0 Registers for fixed size block + 2 * 1 Registers for repeating blocks)
40079 | 40079 | 1 | R | 0x03 | TmpBOM | Back of module temperature measurement | int16 | °C | -1 | Temperature Sensor 1
40080 | 40080 | 1 | R | 0x03 | TmpBOM | Back of module temperature measurement | int16 | °C | -1 | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40081 | 40081 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Base Meteorological Modbus Register Model | uint16 |  |  | 307
40082 | 40082 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 11
40083 | 40083 | 1 | R | 0x03 | TmpAmb | Ambient Temperature | int16 | °C | -1 | Temperature Sensor 2
40084 | 40084 | 1 | R | 0x03 | RH | Relative Humidity | int16 | % |  | not supported
40085 | 40085 | 1 | R | 0x03 | Pres | Barometric Pressure | int16 | Hpa |  | not supported
40086 | 40086 | 1 | R | 0x03 | WndSpd | Wind Speed | int16 | m/s
40087 | 40087 | 1 | R | 0x03 | WndDir | Wind Direction | int16 | deg |  | not supported
40088 | 40088 | 1 | R | 0x03 | Rain | Rainfall | int16 | mm |  | not supported
40089 | 40089 | 1 | R | 0x03 | Snw | Snow Depth | int16 | mm |  | not supported
40090 | 40090 | 1 | R | 0x03 | PPT | Precipitation Type (WMO 4680 SYNOP code reference) | int16 |  |  | not supported
40091 | 40091 | 1 | R | 0x03 | ElecFld | Electric Field | int16 | Vm |  | not supported
40092 | 40092 | 1 | R | 0x03 | SurWet | Surface Wetness | int16 | kO |  | not supported
40093 | 40093 | 1 | R | 0x03 | SoilWet | Soil Wetness | int16 | % |  | not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40094 | 40094 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40095 | 40095 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0

## C001 Common
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 2 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
3 | 3 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
4 | 4 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
5 | 20 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
21 | 36 | 16 | R | 0x03 | Md | Device model | String32
37 | 44 | 8 | R | 0x03 | Opt | Options | String16
45 | 52 | 8 | R | 0x03 | Vr | SW version | String16
53 | 68 | 16 | R | 0x03 | SN | Serialnumber | String32
69 | 69 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247

## 302 Irradiance Model
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Irradiance Modbus Register Model | uint16 |  |  | 302
2 | 2 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 5
3 | 3 | 1 | R | 0x03 | GHI | Global Horizontal Irradiance | uint16 | W / m2
4 | 4 | 1 | R | 0x03 | POAI | Plane-of-Array Irradiance | uint16 | W / m2 |  | not supported
5 | 5 | 1 | R | 0x03 | DFI | Diffuse Irradiance | uint16 | W / m2 |  | not supported
6 | 6 | 1 | R | 0x03 | DNI | Direct Normal Irradiance | uint16 | W / m2 |  | not supported
7 | 7 | 1 | R | 0x03 | OTI | Other Irradiance | uint16 | W / m2 |  | not supported

## 303 Back of Module Temperature Model
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Back of Module Temperature Modbus Register Model | uint16 |  |  | 303
2 | 2 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 2 (0 Registers for fixed size block + 2 * 1 Registers for repeating blocks)
3 | 3 | 1 | R | 0x03 | TmpBOM | Back of module temperature measurement | int16 | °C | -1 | Temperature Sensor 1
4 | 4 | 1 | R | 0x03 | TmpBOM | Back of module temperature measurement | int16 | °C | -1 | Temperature Sensor 2

## 307 meteorological
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Base Meteorological Modbus Register Model | uint16 |  |  | 307
2 | 2 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 11
3 | 3 | 1 | R | 0x03 | TmpAmb | Ambient Temperature | int16 | °C | -1
4 | 4 | 1 | R | 0x03 | RH | Relative Humidity | int16 | % |  | not supported
5 | 5 | 1 | R | 0x03 | Pres | Barometric Pressure | int16 | Hpa |  | not supported
6 | 6 | 1 | R | 0x03 | WndSpd | Wind Speed | int16 | m/s
7 | 7 | 1 | R | 0x03 | WndDir | Wind Direction | int16 | deg |  | not supported
8 | 8 | 1 | R | 0x03 | Rain | Rainfall | int16 | mm |  | not supported
9 | 9 | 1 | R | 0x03 | Snw | Snow Depth | int16 | mm |  | not supported
10 | 10 | 1 | R | 0x03 | PPT | Precipitation Type (WMO 4680 SYNOP code reference) | int16 |  |  | not supported
11 | 11 | 1 | R | 0x03 | ElecFld | Electric Field | int16 | Vm |  | not supported
12 | 12 | 1 | R | 0x03 | SurWet | Surface Wetness | int16 | kO |  | not supported
13 | 13 | 1 | R | 0x03 | SoilWet | Soil Wetness | int16 | % |  | not supported

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0