## Complete Map
Fronius Datamanager Register Map: IG String Control (1, 403)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device model | String32
40037 | 40044 | 8 | R | 0x03 | Opt | Options | String16
40045 | 40052 | 8 | R | 0x03 | Vr | SW version | String16
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber | String32
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec String Combiner Modbus Register Model | uint16 |  |  | 403
40071 | 40071 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 56 (16 Registers for fixed size block + 5 * 8 Registers for repeating blocks)
40072 | 40072 | 1 | R | 0x03 | DCA_SF | Current scale factor | sunssf |  |  | -2
40073 | 40073 | 1 | R | 0x03 | DCAhr_SF | Amp-hour scale factor | sunssf |  |  | -3
40074 | 40074 | 1 | R | 0x03 | DCV_SF | Voltage scale factor | sunssf |  |  | not supported
40075 | 40075 | 1 | R | 0x03 | DCAMax | Maximum DC Current Rating | uint16 | A
40076 | 40076 | 1 | R | 0x03 | N | Number of Inputs | count |  |  | up to 5 Inputs
40077 | 40078 | 2 | R | 0x03 | Evt | Bitmask value. Events | bitfield32 |  |  | 0: no bit set, no event pending 0x8000: bit 15 is set indicating COMM_ERROR
40079 | 40080 | 2 | R | 0x03 | EvtVnd | Bitmask value. Vendor defined events | bitfield32 |  |  | 0: no bit set, no event pending 0x8000: bit 15 is set indicating COMM_ERROR
40081 | 40081 | 1 | R | 0x03 | DCA | Total measured current | int16 | A
40082 | 40083 | 2 | R | 0x03 | DCAhr | Total metered Amp-hours | acc32 | Ah
40084 | 40084 | 1 | R | 0x03 | DCV | Output Voltage | int16 | V |  | not supported
40085 | 40085 | 1 | R | 0x03 | Tmp | Internal operating temperature | int16 | °C |  | not supported
40086 | 40086 | 1 | R | 0x03 | InDCA_SF | Current scale factor for inputs | sunssf |  |  | -3
40087 | 40087 | 1 | R | 0x03 | InDCAhr_SF | Amp-hour scale factor for inputs | sunssf |  |  | -3
40088 | 40088 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 1
40089 | 40090 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40091 | 40092 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40093 | 40093 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
40094 | 40095 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
40096 | 40096 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 2
40097 | 40098 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40099 | 40100 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40101 | 40101 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
40102 | 40103 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
40104 | 40104 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 3
40105 | 40106 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40107 | 40108 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40109 | 40109 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
40110 | 40111 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
40112 | 40112 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 4
40113 | 40114 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40115 | 40116 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40117 | 40117 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
40118 | 40119 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
40120 | 40120 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 5
40121 | 40122 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40123 | 40124 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40125 | 40125 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
40126 | 40127 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40128 | 40128 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40129 | 40129 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0

## C001 Common
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 2 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
3 | 3 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
4 | 4 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
5 | 20 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
21 | 36 | 16 | R | 0x03 | Md | Device model | String32
37 | 44 | 8 | R | 0x03 | Opt | Options | String16
45 | 52 | 8 | R | 0x03 | Vr | SW version | String16
53 | 68 | 16 | R | 0x03 | SN | Serialnumber | String32
69 | 69 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247

## 403 string_combiner
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec String Combiner Modbus Register Model | uint16 |  |  | 403
2 | 2 | 1 | R | 0x03 | L | Length of Register Model | uint16 | Registers |  | 56 (16 Registers for fixed size block + 5 * 8 Registers for repeating blocks)
3 | 3 | 1 | R | 0x03 | DCA_SF | Current scale factor | sunssf |  |  | -2
4 | 4 | 1 | R | 0x03 | DCAhr_SF | Amp-hour scale factor | sunssf |  |  | -3
5 | 5 | 1 | R | 0x03 | DCV_SF | Voltage scale factor | sunssf |  |  | not supported
6 | 6 | 1 | R | 0x03 | DCAMax | Maximum DC Current Rating | uint16 | A
7 | 7 | 1 | R | 0x03 | N | Number of Inputs | count |  |  | up to 5 Inputs
8 | 9 | 2 | R | 0x03 | Evt | Bitmask value. Events | bitfield32 |  |  | 0: no bit set, no event pending 0x8000: bit 15 is set indicating COMM_ERROR
10 | 11 | 2 | R | 0x03 | EvtVnd | Bitmask value. Vendor defined events | bitfield32 |  |  | 0: no bit set, no event pending 0x8000: bit 15 is set indicating COMM_ERROR
12 | 12 | 1 | R | 0x03 | DCA | Total measured current | int16 | A
13 | 14 | 2 | R | 0x03 | DCAhr | Total metered Amp-hours | acc32 | Ah
15 | 15 | 1 | R | 0x03 | DCV | Output Voltage | int16 | V |  | not supported
16 | 16 | 1 | R | 0x03 | Tmp | Internal operating temperature | int16 | °C |  | not supported
17 | 17 | 1 | R | 0x03 | InDCA_SF | Current scale factor for inputs | sunssf |  |  | -3
18 | 18 | 1 | R | 0x03 | InDCAhr_SF | Amp-hour scale factor for inputs | sunssf |  |  | -3
19 | 19 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 1
20 | 21 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
22 | 23 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
24 | 24 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
25 | 26 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
27 | 27 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 2
28 | 29 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
30 | 31 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
32 | 32 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
33 | 34 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
35 | 35 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 3
36 | 37 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
38 | 39 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
40 | 40 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
41 | 42 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
43 | 43 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 4
44 | 45 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
46 | 47 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
48 | 48 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
49 | 50 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah
51 | 51 | 1 | R | 0x03 | InID | Uniquely identifies this input set | uint16 |  |  | 5
52 | 53 | 2 | R | 0x03 | InEvt | String Input Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
54 | 55 | 2 | R | 0x03 | InEvtVnd | String Input Vendor Event Flags | bitfield32 |  |  | Always 0, no bit set, no event pending
56 | 56 | 1 | R | 0x03 | InDCA | String Input Current | int16 | A
57 | 58 | 2 | R | 0x03 | InDCAhr | String Input Amp-Hours | acc32 | Ah

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0