## Complete Map
Fronius Datamanager Register Map: Floating Point Meter Model (211, 212, 213)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device model | String32
40037 | 40044 | 8 | R | 0x03 | Opt | Options | String16
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of meter | String16
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the meter | String32
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Meter Modbus Map (float); 211: single phase, 212: split phase, 213: three phase | uint16 |  |  | 211, 212, 213
40071 | 40071 | 1 | R | 0x03 | L | Length of inverter model block | uint16 | Registers |  | 124
40072 | 40073 | 2 | R | 0x03 | A | AC Total Current value | float32 | A
40074 | 40075 | 2 | R | 0x03 | AphA | AC Phase-A Current value | float32 | A
40076 | 40077 | 2 | R | 0x03 | AphB | AC Phase-B Current value | float32 | A
40078 | 40079 | 2 | R | 0x03 | AphC | AC Phase-C Current value | float32 | A
40080 | 40081 | 2 | R | 0x03 | PhV | AC Voltage Average Phase-to-neutral value | float32 | V
40082 | 40083 | 2 | R | 0x03 | PhVphA | AC Voltage Phase-A-to-neutral value | float32 | V
40084 | 40085 | 2 | R | 0x03 | PhVphB | AC Voltage Phase-B-to-neutral value | float32 | V
40086 | 40087 | 2 | R | 0x03 | PhVphC | AC Voltage Phase-C-to-neutral value | float32 | V
40088 | 40089 | 2 | R | 0x03 | PPV | AC Voltage Average Phase-to-phase value | float32 | V
40090 | 40091 | 2 | R | 0x03 | PPVphAB | AC Voltage Phase-AB value | float32 | V
40092 | 40093 | 2 | R | 0x03 | PPVphBC | AC Voltage Phase-BC value | float32 | V
40094 | 40095 | 2 | R | 0x03 | PPVphCA | AC Voltage Phase-CA value | float32 | V
40096 | 40097 | 2 | R | 0x03 | Hz | AC Frequency value | float32 | Hz
40098 | 40099 | 2 | R | 0x03 | W | AC Power value | float32 | W
40100 | 40101 | 2 | R | 0x03 | WphA | AC Power Phase A value | float32 | W
40102 | 40103 | 2 | R | 0x03 | WphB | AC Power Phase B value | float32 | W
40104 | 40105 | 2 | R | 0x03 | WphC | AC Power Phase C value | float32 | W
40106 | 40107 | 2 | R | 0x03 | VA | AC Apparent Power value | float32 | VA
40108 | 40109 | 2 | R | 0x03 | VAphA | AC Apparent Power Phase A value | float32 | VA
40110 | 40111 | 2 | R | 0x03 | VAphB | AC Apparent Power Phase B value | float32 | VA
40112 | 40113 | 2 | R | 0x03 | VAphC | AC Apparent Power Phase C value | float32 | VA
40114 | 40115 | 2 | R | 0x03 | VAR | AC Reactive Power value | float32 | VAr
40116 | 40117 | 2 | R | 0x03 | VARphA | AC Reactive Power Phase A value | float32 | VAr
40118 | 40119 | 2 | R | 0x03 | VARphB | AC Reactive Power Phase B value | float32 | VAr
40120 | 40121 | 2 | R | 0x03 | VARphC | AC Reactive Power Phase C value | float32 | VAr
40122 | 40123 | 2 | R | 0x03 | PF | Power Factor value | float32 | cos()
40124 | 40125 | 2 | R | 0x03 | PFphA | Power Factor Phase A value | float32 | cos()
40126 | 40127 | 2 | R | 0x03 | PFphB | Power Factor Phase B value | float32 | cos()
40128 | 40129 | 2 | R | 0x03 | PFphC | Power Factor Phase C value | float32 | cos()
40130 | 40131 | 2 | R | 0x03 | TotWhExp | Total Watt-hours Exported | float32 | Wh
40132 | 40133 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | float32 | Wh |  | register not supported
40134 | 40135 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | float32 | Wh |  | register not supported
40136 | 40137 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | float32 | Wh |  | register not supported
40138 | 40139 | 2 | R | 0x03 | TotWhImp | Total Watt-hours Imported | float32 | Wh
40140 | 40141 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | float32 | Wh |  | register not supported
40142 | 40143 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | float32 | Wh |  | register not supported
40144 | 40145 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | float32 | Wh |  | register not supported
40146 | 40147 | 2 | R | 0x03 | TotVAhExp | Total VA-hours Exported | float32 | VAh
40148 | 40149 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | float32 | VAh |  | register not supported
40150 | 40151 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | float32 | VAh |  | register not supported
40152 | 40153 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | float32 | VAh |  | register not supported
40154 | 40155 | 2 | R | 0x03 | TotVAhImp | Total VA-hours Imported | float32 | VAh
40156 | 40157 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | float32 | VAh |  | register not supported
40158 | 40159 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | float32 | VAh |  | register not supported
40160 | 40161 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | float32 | VAh |  | register not supported
40162 | 40163 | 2 | R | 0x03 | TotVArhImpQ1 | Total VAR-hours Imported Q1 | float32 | VArh |  | register not supported
40164 | 40165 | 2 | R | 0x03 | TotVArhImpQ1phA | Total VAR-hours Imported Q1 phase A | float32 | VArh |  | register not supported
40166 | 40167 | 2 | R | 0x03 | TotVArhImpQ1phB | Total VAR-hours Imported Q1 phase B | float32 | VArh |  | register not supported
40168 | 40169 | 2 | R | 0x03 | TotVArhImpQ1phC | Total VAR-hours Imported Q1 phase C | float32 | VArh |  | register not supported
40170 | 40171 | 2 | R | 0x03 | TotVArhImpQ2 | Total VAr-hours Imported Q2 | float32 | VArh |  | register not supported
40172 | 40173 | 2 | R | 0x03 | TotVArhImpQ2phA | Total VAR-hours Imported Q2 phase A | float32 | VArh |  | register not supported
40174 | 40175 | 2 | R | 0x03 | TotVArhImpQ2phB | Total VAR-hours Imported Q2 phase B | float32 | VArh |  | register not supported
40176 | 40177 | 2 | R | 0x03 | TotVArhImpQ2phC | Total VAR-hours Imported Q2 phase C | float32 | VArh |  | register not supported
40178 | 40179 | 2 | R | 0x03 | TotVArhExpQ3 | Total VAr-hours Exported Q3 | float32 | VArh |  | register not supported
40180 | 40181 | 2 | R | 0x03 | TotVArhExpQ3phA | Total VAR-hours Exported Q3 phase A | float32 | VArh |  | register not supported
40182 | 40183 | 2 | R | 0x03 | TotVArhExpQ3phB | Total VAR-hours Exported Q3 phase B | float32 | VArh |  | register not supported
40184 | 40185 | 2 | R | 0x03 | TotVArhExpQ3phC | Total VAR-hours Exported Q3 phase C | float32 | VArh |  | register not supported
40186 | 40187 | 2 | R | 0x03 | TotVArhExpQ4 | Total VAr-hours Exported Q4 | float32 | VArh |  | register not supported
40188 | 40189 | 2 | R | 0x03 | TotVArhExpQ4phA | Total VAR-hours Exported Q4 phase A | float32 | VArh |  | register not supported
40190 | 40191 | 2 | R | 0x03 | TotVArhExpQ4phB | Total VAR-hours Exported Q4 phase B | float32 | VArh |  | register not supported
40192 | 40193 | 2 | R | 0x03 | TotVArhExpQ4phC | Total VAR-hours Exported Q4 phase C | float32 | VArh |  | register not supported
40194 | 40195 | 2 | R | 0x03 | Evt | Events | bitfield32
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40196 | 40196 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40197 | 40197 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0

## C001 Common
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 2 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
3 | 3 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
4 | 4 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
5 | 20 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
21 | 36 | 16 | R | 0x03 | Md | Device model | String32
37 | 44 | 8 | R | 0x03 | Opt | Options | String16
45 | 52 | 8 | R | 0x03 | Vr | SW version of meter | String16
53 | 68 | 16 | R | 0x03 | SN | Serialnumber of the meter | String32
69 | 69 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1-247

## M21X Meter
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Meter Modbus Map (float); 211: single phase, 212: split phase, 213: three phase | uint16 |  |  | 211, 212, 213
2 | 2 | 1 | R | 0x03 | L | Length of inverter model block | uint16 | Registers |  | 124
3 | 4 | 2 | R | 0x03 | A | AC Total Current value | float32 | A
5 | 6 | 2 | R | 0x03 | AphA | AC Phase-A Current value | float32 | A
7 | 8 | 2 | R | 0x03 | AphB | AC Phase-B Current value | float32 | A
9 | 10 | 2 | R | 0x03 | AphC | AC Phase-C Current value | float32 | A
11 | 12 | 2 | R | 0x03 | PhV | AC Voltage Average Phase-to-neutral value | float32 | V
13 | 14 | 2 | R | 0x03 | PhVphA | AC Voltage Phase-A-to-neutral value | float32 | V
15 | 16 | 2 | R | 0x03 | PhVphB | AC Voltage Phase-B-to-neutral value | float32 | V
17 | 18 | 2 | R | 0x03 | PhVphC | AC Voltage Phase-C-to-neutral value | float32 | V
19 | 20 | 2 | R | 0x03 | PPV | AC Voltage Average Phase-to-phase value | float32 | V
21 | 22 | 2 | R | 0x03 | PPVphAB | AC Voltage Phase-AB value | float32 | V
23 | 24 | 2 | R | 0x03 | PPVphBC | AC Voltage Phase-BC value | float32 | V
25 | 26 | 2 | R | 0x03 | PPVphCA | AC Voltage Phase-CA value | float32 | V
27 | 28 | 2 | R | 0x03 | Hz | AC Frequency value | float32 | Hz
29 | 30 | 2 | R | 0x03 | W | AC Power value | float32 | W
31 | 32 | 2 | R | 0x03 | WphA | AC Power Phase A value | float32 | W
33 | 34 | 2 | R | 0x03 | WphB | AC Power Phase B value | float32 | W
35 | 36 | 2 | R | 0x03 | WphC | AC Power Phase C value | float32 | W
37 | 38 | 2 | R | 0x03 | VA | AC Apparent Power value | float32 | VA
39 | 40 | 2 | R | 0x03 | VAphA | AC Apparent Power Phase A value | float32 | VA
41 | 42 | 2 | R | 0x03 | VAphB | AC Apparent Power Phase B value | float32 | VA
43 | 44 | 2 | R | 0x03 | VAphC | AC Apparent Power Phase C value | float32 | VA
45 | 46 | 2 | R | 0x03 | VAR | AC Reactive Power value | float32 | VAr
47 | 48 | 2 | R | 0x03 | VARphA | AC Reactive Power Phase A value | float32 | VAr
49 | 50 | 2 | R | 0x03 | VARphB | AC Reactive Power Phase B value | float32 | VAr
51 | 52 | 2 | R | 0x03 | VARphC | AC Reactive Power Phase C value | float32 | VAr
53 | 54 | 2 | R | 0x03 | PF | Power Factor value | float32 | cos()
55 | 56 | 2 | R | 0x03 | PFphA | Power Factor Phase A value | float32 | cos()
57 | 58 | 2 | R | 0x03 | PFphB | Power Factor Phase B value | float32 | cos()
59 | 60 | 2 | R | 0x03 | PFphC | Power Factor Phase C value | float32 | cos()
61 | 62 | 2 | R | 0x03 | TotWhExp | Total Watt-hours Exported | uint32 | Wh
63 | 64 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | uint32 | Wh |  | register not supported
65 | 66 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | uint32 | Wh |  | register not supported
67 | 68 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | uint32 | Wh |  | register not supported
69 | 70 | 2 | R | 0x03 | TotWhImp | Total Watt-hours Imported | uint32 | Wh
71 | 72 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | uint32 | Wh |  | register not supported
73 | 74 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | uint32 | Wh |  | register not supported
75 | 76 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | uint32 | Wh |  | register not supported
77 | 78 | 2 | R | 0x03 | TotVAhExp | Total VA-hours Exported | uint32 | VAh
79 | 80 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | uint32 | VAh |  | register not supported
81 | 82 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | uint32 | VAh |  | register not supported
83 | 84 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | uint32 | VAh |  | register not supported
85 | 86 | 2 | R | 0x03 | TotVAhImp | Total VA-hours Imported | uint32 | VAh
87 | 88 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | uint32 | VAh |  | register not supported
89 | 90 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | uint32 | VAh |  | register not supported
91 | 92 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | uint32 | VAh |  | register not supported
93 | 94 | 2 | R | 0x03 | TotVArhImpQ1 | Total VAR-hours Imported Q1 | uint32 | VArh |  | register not supported
95 | 96 | 2 | R | 0x03 | TotVArhImpQ1phA | Total VAR-hours Imported Q1 phase A | uint32 | VArh |  | register not supported
97 | 98 | 2 | R | 0x03 | TotVArhImpQ1phB | Total VAR-hours Imported Q1 phase B | uint32 | VArh |  | register not supported
99 | 100 | 2 | R | 0x03 | TotVArhImpQ1phC | Total VAR-hours Imported Q1 phase C | uint32 | VArh |  | register not supported
101 | 102 | 2 | R | 0x03 | TotVArhImpQ2 | Total VAr-hours Imported Q2 | uint32 | VArh |  | register not supported
103 | 104 | 2 | R | 0x03 | TotVArhImpQ2phA | Total VAR-hours Imported Q2 phase A | uint32 | VArh |  | register not supported
105 | 106 | 2 | R | 0x03 | TotVArhImpQ2phB | Total VAR-hours Imported Q2 phase B | uint32 | VArh |  | register not supported
107 | 108 | 2 | R | 0x03 | TotVArhImpQ2phC | Total VAR-hours Imported Q2 phase C | uint32 | VArh |  | register not supported
109 | 110 | 2 | R | 0x03 | TotVArhExpQ3 | Total VAr-hours Exported Q3 | uint32 | VArh |  | register not supported
111 | 112 | 2 | R | 0x03 | TotVArhExpQ3phA | Total VAR-hours Exported Q3 phase A | uint32 | VArh |  | register not supported
113 | 114 | 2 | R | 0x03 | TotVArhExpQ3phB | Total VAR-hours Exported Q3 phase B | uint32 | VArh |  | register not supported
115 | 116 | 2 | R | 0x03 | TotVArhExpQ3phC | Total VAR-hours Exported Q3 phase C | uint32 | VArh |  | register not supported
117 | 118 | 2 | R | 0x03 | TotVArhExpQ4 | Total VAr-hours Exported Q4 | uint32 | VArh |  | register not supported
119 | 120 | 2 | R | 0x03 | TotVArhExpQ4phA | Total VAR-hours Exported Q4 phase A | uint32 | VArh |  | register not supported
121 | 122 | 2 | R | 0x03 | TotVArhExpQ4phB | Total VAR-hours Exported Q4 phase B | uint32 | VArh |  | register not supported
123 | 124 | 2 | R | 0x03 | TotVArhExpQ4phC | Total VAR-hours Exported Q4 phase C | uint32 | VArh |  | register not supported
125 | 126 | 2 | R | 0x03 | Evt | Events | uint32

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0